## summary
Metric | Value
Start Time | 2025-10-21 16:01
End Time | 2025-10-22 16:00
Duration (hours) | 23.98
Total Samples | 1,440
Dominant Interval (s) | 60.0
Dominant Interval (min) | 1.00
Mixed Sampling | NO
Dominant Ratio | 99.9%
Energy (kWh) | 1691.71
Power Mean (W) | 70488.0
Power Min (W) | 25624.5
Power Max (W) | 91708.8
E_total (kWh) | 1691.71
E_phase_sum (kWh) | 1691.89
Delta E (%) | 0.01
Status | PASS
PF Calculated Mean | 0.881
PF Measured Mean | 0.881
¦ΔPF¦ Mean | 0.0060
¦ΔPF¦ P95 | 0.0147
Mean (Hz) | 50.006
Min (Hz) | 49.925
Max (Hz) | 50.054
Std Dev (Hz) | 0.0187
Mean (%) | 0.59
P95 (%) | 0.78
Max (%) | 0.96
delta_E | PASS
PF_diff | PASS
overall | PASS

## validation
Validation | Value
P: Sum of Phases vs Total
Mean Rel Error | 0.0060
P95 Rel Error | 0.0227
Max Rel Error | 0.0526
S: Sum of Phases vs Total
Mean Rel Error | 0.0058
P95 Rel Error | 0.0200
Vector Validation (S² = P² + Q²)
Samples Used | 1,440
Mean Rel Error | 0.0061
P95 Rel Error | 0.0148

## timeseries_power
timestamp | P_total | S_total | Q_total | PF_total | PF_calc | P_L1N | P_L2N | P_L3N | S_L1N | S_L2N | S_L3N | Q_L1N | Q_L2N | Q_L3N | U_L1N | U_L2N | U_L3N | F
2025-10-21 16:01 | 83616.805 | 97103.383 | -47203.031 | 0.87 | 0.86111 | 29670.479 | 25624.504 | 28321.82 | 33716.453 | 31019.137 | 31019.137 | -16183.896 | -16183.896 | -13486.581 | 228.511 | 230.108 | 231.403 | 49.999
2025-10-21 16:02 | 84965.461 | 97103.383 | -45854.375 | 0.87 | 0.875 | 29670.479 | 26973.162 | 28321.82 | 33716.453 | 31019.137 | 31019.137 | -16183.896 | -16183.896 | -13486.581 | 227.691 | 229.266 | 230.798 | 50.007
2025-10-21 16:03 | 87662.773 | 99800.695 | -48551.691 | 0.87 | 0.87838 | 31019.137 | 26973.162 | 29670.479 | 35065.109 | 32367.793 | 32367.793 | -17532.555 | -17532.555 | -13486.581 | 225.792 | 227.303 | 228.856 | 50.022
2025-10-21 16:04 | 82268.141 | 93057.406 | -45854.375 | 0.87 | 0.88406 | 28321.82 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 225.857 | 227.346 | 228.727 | 50.034
2025-10-21 16:05 | 86314.117 | 98452.039 | -45854.375 | 0.88 | 0.87671 | 31019.137 | 26973.162 | 29670.479 | 35065.109 | 31019.137 | 32367.793 | -17532.555 | -16183.896 | -13486.581 | 226.18 | 227.303 | 228.899 | 50.034
2025-10-21 16:06 | 83616.805 | 95754.727 | -44505.715 | 0.88 | 0.87324 | 29670.479 | 25624.504 | 28321.82 | 33716.453 | 29670.479 | 31019.137 | -16183.896 | -16183.896 | -12137.923 | 225.727 | 226.59 | 228.425 | 50.029
2025-10-21 16:07 | 84965.461 | 97103.383 | -45854.375 | 0.88 | 0.875 | 29670.479 | 26973.162 | 28321.82 | 35065.109 | 31019.137 | 31019.137 | -16183.896 | -16183.896 | -13486.581 | 225.878 | 227.173 | 228.511 | 50.016
2025-10-21 16:08 | 83616.805 | 95754.727 | -44505.715 | 0.88 | 0.87324 | 29670.479 | 25624.504 | 28321.82 | 33716.453 | 31019.137 | 31019.137 | -16183.896 | -16183.896 | -12137.923 | 226.008 | 227.518 | 228.641 | 50.016
2025-10-21 16:09 | 80919.484 | 93057.406 | -45854.375 | 0.87 | 0.86957 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 225.9 | 227.41 | 228.619 | 50.019
2025-10-21 16:10 | 84965.461 | 97103.383 | -47203.031 | 0.87 | 0.875 | 29670.479 | 28321.82 | 28321.82 | 33716.453 | 32367.793 | 31019.137 | -16183.896 | -17532.555 | -13486.581 | 225.166 | 226.396 | 228.058 | 50.006
2025-10-21 16:11 | 89011.43 | 99800.695 | -47203.031 | 0.88 | 0.89189 | 31019.137 | 28321.82 | 28321.82 | 35065.109 | 33716.453 | 31019.137 | -16183.896 | -17532.555 | -13486.581 | 225.684 | 227.065 | 228.684 | 50.005
2025-10-21 16:12 | 89011.43 | 101149.359 | -47203.031 | 0.88 | 0.88 | 31019.137 | 28321.82 | 28321.82 | 35065.109 | 33716.453 | 32367.793 | -17532.555 | -17532.555 | -13486.581 | 225.576 | 227 | 228.533 | 49.993
2025-10-21 16:13 | 82268.141 | 93057.406 | -43157.059 | 0.88 | 0.88406 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 31019.137 | 29670.479 | -14835.239 | -16183.896 | -12137.923 | 225.922 | 227.389 | 228.878 | 50.009
2025-10-21 16:14 | 83616.805 | 95754.727 | -44505.715 | 0.88 | 0.87324 | 29670.479 | 26973.162 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.102 | 226.159 | 228.144 | 50.003
2025-10-21 16:15 | 78222.172 | 90360.094 | -44505.715 | 0.87 | 0.86567 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 225.037 | 226.375 | 228.403 | 49.986
2025-10-21 16:16 | 76873.508 | 87662.773 | -40459.742 | 0.88 | 0.87692 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -10789.265 | 225.36 | 226.396 | 228.403 | 49.989
2025-10-21 16:17 | 79570.828 | 91708.75 | -43157.059 | 0.87 | 0.86765 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 28321.82 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 225.36 | 226.418 | 228.209 | 50.013
2025-10-21 16:18 | 78222.172 | 90360.094 | -43157.059 | 0.87 | 0.86567 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 224.54 | 225.9 | 227.497 | 49.999
2025-10-21 16:19 | 82268.141 | 93057.406 | -44505.715 | 0.88 | 0.88406 | 29670.479 | 25624.504 | 28321.82 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.433 | 225.9 | 227.41 | 50.004
2025-10-21 16:20 | 79570.828 | 91708.75 | -43157.059 | 0.88 | 0.86765 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 224.778 | 226.677 | 227.756 | 50.001
2025-10-21 16:21 | 72827.539 | 83616.805 | -40459.742 | 0.87 | 0.87097 | 25624.504 | 22927.188 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 224.519 | 226.483 | 227.044 | 49.995
2025-10-21 16:22 | 74176.195 | 84965.461 | -40459.742 | 0.87 | 0.87302 | 26973.162 | 22927.188 | 24275.846 | 31019.137 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 224.001 | 225.598 | 226.612 | 50
2025-10-21 16:23 | 68781.563 | 80919.484 | -39111.086 | 0.86 | 0.85 | 25624.504 | 21578.529 | 22927.188 | 29670.479 | 25624.504 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 223.764 | 224.605 | 226.137 | 49.995
2025-10-21 16:24 | 71478.875 | 83616.805 | -40459.742 | 0.87 | 0.85484 | 24275.846 | 24275.846 | 22927.188 | 28321.82 | 28321.82 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 224.54 | 225.08 | 227.303 | 49.986
2025-10-21 16:25 | 74176.195 | 83616.805 | -39111.086 | 0.88 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 223.742 | 224.238 | 226.461 | 49.981
2025-10-21 16:26 | 79570.828 | 91708.75 | -44505.715 | 0.87 | 0.86765 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 224.195 | 224.821 | 226.677 | 49.972
2025-10-21 16:27 | 74176.195 | 86314.117 | -41808.402 | 0.87 | 0.85938 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 29670.479 | 26973.162 | -14835.239 | -16183.896 | -10789.265 | 225.404 | 226.267 | 228.123 | 49.981
2025-10-21 16:28 | 76873.508 | 86314.117 | -37762.426 | 0.89 | 0.89062 | 25624.504 | 25624.504 | 25624.504 | 28321.82 | 29670.479 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 225.166 | 226.18 | 228.144 | 49.981
2025-10-21 16:29 | 79570.828 | 89011.43 | -40459.742 | 0.89 | 0.89394 | 25624.504 | 28321.82 | 25624.504 | 29670.479 | 32367.793 | 28321.82 | -13486.581 | -14835.239 | -12137.923 | 225.102 | 226.116 | 228.166 | 49.976
2025-10-21 16:30 | 75524.852 | 86314.117 | -39111.086 | 0.89 | 0.875 | 24275.846 | 26973.162 | 24275.846 | 28321.82 | 31019.137 | 26973.162 | -13486.581 | -14835.239 | -10789.265 | 224.67 | 225.663 | 227.691 | 49.978
2025-10-21 16:31 | 72827.539 | 83616.805 | -39111.086 | 0.88 | 0.87097 | 24275.846 | 25624.504 | 22927.188 | 28321.82 | 29670.479 | 25624.504 | -13486.581 | -14835.239 | -10789.265 | 224.454 | 225.555 | 227.065 | 49.981
2025-10-21 16:32 | 70130.219 | 79570.828 | -37762.426 | 0.88 | 0.88136 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 224.476 | 225.576 | 226.763 | 50.003
2025-10-21 16:33 | 72827.539 | 82268.141 | -36413.77 | 0.9 | 0.88525 | 24275.846 | 25624.504 | 24275.846 | 26973.162 | 28321.82 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 224.368 | 225.49 | 226.612 | 50.001
2025-10-21 16:34 | 78222.172 | 87662.773 | -40459.742 | 0.89 | 0.89231 | 26973.162 | 25624.504 | 25624.504 | 29670.479 | 29670.479 | 28321.82 | -13486.581 | -14835.239 | -12137.923 | 225.058 | 226.418 | 227.691 | 49.999
2025-10-21 16:35 | 78222.172 | 87662.773 | -40459.742 | 0.89 | 0.89231 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -14835.239 | -13486.581 | -12137.923 | 223.958 | 225.253 | 226.526 | 50.014
2025-10-21 16:36 | 82268.141 | 93057.406 | -43157.059 | 0.88 | 0.88406 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 223.915 | 224.95 | 226.439 | 50.008
2025-10-21 16:37 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 29670.479 | 25624.504 | 28321.82 | 33716.453 | 31019.137 | 31019.137 | -16183.896 | -16183.896 | -13486.581 | 225.08 | 226.353 | 227.799 | 49.997
2025-10-21 16:38 | 78222.172 | 91708.75 | -47203.031 | 0.85 | 0.85294 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 225.123 | 226.979 | 227.928 | 49.995
2025-10-21 16:39 | 78222.172 | 91708.75 | -45854.375 | 0.86 | 0.85294 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 225.317 | 227.195 | 228.123 | 49.985
2025-10-21 16:40 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 31019.137 | 31019.137 | -16183.896 | -16183.896 | -13486.581 | 224.907 | 226.957 | 227.842 | 49.981
2025-10-21 16:41 | 86314.117 | 98452.039 | -47203.031 | 0.88 | 0.87671 | 31019.137 | 26973.162 | 28321.82 | 35065.109 | 32367.793 | 31019.137 | -16183.896 | -16183.896 | -13486.581 | 224.799 | 226.396 | 227.626 | 49.988
2025-10-21 16:42 | 86314.117 | 98452.039 | -47203.031 | 0.88 | 0.87671 | 31019.137 | 26973.162 | 28321.82 | 35065.109 | 32367.793 | 32367.793 | -16183.896 | -16183.896 | -13486.581 | 224.54 | 226.18 | 227.54 | 49.985
2025-10-21 16:43 | 83616.805 | 95754.727 | -45854.375 | 0.88 | 0.87324 | 29670.479 | 26973.162 | 28321.82 | 33716.453 | 31019.137 | 31019.137 | -16183.896 | -16183.896 | -13486.581 | 224.778 | 226.375 | 228.036 | 49.997
2025-10-21 16:44 | 80919.484 | 93057.406 | -44505.715 | 0.87 | 0.86957 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 223.591 | 225.468 | 226.569 | 50.004
2025-10-21 16:45 | 82268.141 | 95754.727 | -45854.375 | 0.87 | 0.85915 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 224.799 | 226.612 | 227.799 | 49.99
2025-10-21 16:46 | 82268.141 | 94406.063 | -43157.059 | 0.88 | 0.87143 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.037 | 226.742 | 228.23 | 50.007
2025-10-21 16:47 | 83616.805 | 94406.063 | -44505.715 | 0.88 | 0.88571 | 29670.479 | 26973.162 | 26973.162 | 33716.453 | 32367.793 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.217 | 225.77 | 227.087 | 50.013
2025-10-21 16:48 | 83616.805 | 95754.727 | -45854.375 | 0.87 | 0.87324 | 29670.479 | 26973.162 | 26973.162 | 33716.453 | 32367.793 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 225.231 | 226.526 | 227.864 | 50.008
2025-10-21 16:49 | 84965.461 | 97103.383 | -45854.375 | 0.88 | 0.875 | 29670.479 | 28321.82 | 26973.162 | 33716.453 | 32367.793 | 31019.137 | -16183.896 | -16183.896 | -13486.581 | 224.605 | 226.137 | 227.432 | 50.021
2025-10-21 16:50 | 78222.172 | 90360.094 | -43157.059 | 0.87 | 0.86567 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -14835.239 | -16183.896 | -12137.923 | 225.425 | 226.461 | 227.756 | 50.025
2025-10-21 16:51 | 79570.828 | 90360.094 | -43157.059 | 0.87 | 0.8806 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 225.749 | 226.936 | 228.209 | 50.038
2025-10-21 16:52 | 80919.484 | 91708.75 | -43157.059 | 0.88 | 0.88235 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.339 | 226.655 | 227.972 | 50.013
2025-10-21 16:53 | 82268.141 | 91708.75 | -41808.402 | 0.89 | 0.89706 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 31019.137 | 29670.479 | -14835.239 | -14835.239 | -10789.265 | 224.433 | 226.073 | 227.367 | 50.004
2025-10-21 16:54 | 78222.172 | 89011.43 | -40459.742 | 0.89 | 0.87879 | 28321.82 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -10789.265 | 224.735 | 226.979 | 227.562 | 49.998
2025-10-21 16:55 | 84965.461 | 95754.727 | -43157.059 | 0.89 | 0.88732 | 29670.479 | 26973.162 | 28321.82 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 224.756 | 226.418 | 227.885 | 50.007
2025-10-21 16:56 | 75524.852 | 86314.117 | -40459.742 | 0.88 | 0.875 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 224.95 | 225.986 | 227.756 | 50.004
2025-10-21 16:57 | 78222.172 | 89011.43 | -41808.402 | 0.88 | 0.87879 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -16183.896 | -14835.239 | -10789.265 | 224.411 | 225.857 | 227.108 | 49.999
2025-10-21 16:58 | 80919.484 | 91708.75 | -41808.402 | 0.88 | 0.88235 | 28321.82 | 26973.162 | 25624.504 | 32367.793 | 32367.793 | 28321.82 | -14835.239 | -16183.896 | -10789.265 | 225.058 | 226.267 | 227.95 | 50.001
2025-10-21 16:59 | 83616.805 | 93057.406 | -41808.402 | 0.89 | 0.89855 | 28321.82 | 28321.82 | 26973.162 | 32367.793 | 32367.793 | 28321.82 | -14835.239 | -16183.896 | -10789.265 | 222.426 | 223.634 | 225.123 | 50.017
2025-10-21 17:00 | 83616.805 | 94406.063 | -41808.402 | 0.89 | 0.88571 | 28321.82 | 28321.82 | 26973.162 | 32367.793 | 32367.793 | 28321.82 | -14835.239 | -16183.896 | -10789.265 | 224.843 | 225.792 | 227.346 | 50.016
2025-10-21 17:01 | 80919.484 | 93057.406 | -43157.059 | 0.88 | 0.86957 | 28321.82 | 26973.162 | 25624.504 | 32367.793 | 32367.793 | 28321.82 | -16183.896 | -16183.896 | -10789.265 | 226.698 | 227.346 | 229.202 | 50.013
2025-10-21 17:02 | 79570.828 | 90360.094 | -44505.715 | 0.87 | 0.8806 | 26973.162 | 26973.162 | 25624.504 | 31019.137 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 227.367 | 228.662 | 230.432 | 50.034
2025-10-21 17:03 | 82268.141 | 93057.406 | -45854.375 | 0.87 | 0.88406 | 28321.82 | 28321.82 | 25624.504 | 32367.793 | 32367.793 | 28321.82 | -16183.896 | -17532.555 | -12137.923 | 227.907 | 229.309 | 230.928 | 50.039
2025-10-21 17:04 | 83616.805 | 94406.063 | -43157.059 | 0.88 | 0.88571 | 28321.82 | 28321.82 | 26973.162 | 32367.793 | 32367.793 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 227.583 | 228.921 | 230.669 | 50.038
2025-10-21 17:05 | 78222.172 | 89011.43 | -40459.742 | 0.89 | 0.87879 | 26973.162 | 25624.504 | 25624.504 | 29670.479 | 29670.479 | 28321.82 | -14835.239 | -13486.581 | -12137.923 | 228.943 | 230.302 | 231.791 | 50.025
2025-10-21 17:06 | 76873.508 | 86314.117 | -37762.426 | 0.89 | 0.89062 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 28321.82 | 28321.82 | -13486.581 | -13486.581 | -10789.265 | 229.202 | 230.129 | 231.597 | 50.025
2025-10-21 17:07 | 75524.852 | 84965.461 | -37762.426 | 0.89 | 0.88889 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 228.058 | 229.396 | 230.906 | 50.007
2025-10-21 17:08 | 74176.195 | 83616.805 | -37762.426 | 0.89 | 0.8871 | 24275.846 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 228.101 | 229.007 | 230.906 | 49.986
2025-10-21 17:09 | 72827.539 | 82268.141 | -39111.086 | 0.88 | 0.88525 | 24275.846 | 25624.504 | 22927.188 | 26973.162 | 29670.479 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 228.144 | 229.094 | 231.144 | 49.977
2025-10-21 17:10 | 72827.539 | 82268.141 | -39111.086 | 0.88 | 0.88525 | 24275.846 | 25624.504 | 22927.188 | 28321.82 | 28321.82 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 228.856 | 229.137 | 231.575 | 49.967
2025-10-21 17:11 | 74176.195 | 82268.141 | -36413.77 | 0.9 | 0.90164 | 22927.188 | 26973.162 | 24275.846 | 26973.162 | 29670.479 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 229.029 | 229.245 | 231.467 | 49.967
2025-10-21 17:12 | 79570.828 | 89011.43 | -41808.402 | 0.88 | 0.89394 | 25624.504 | 28321.82 | 25624.504 | 29670.479 | 31019.137 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 228.921 | 229.655 | 231.877 | 49.984
2025-10-21 17:13 | 70130.219 | 80919.484 | -39111.086 | 0.87 | 0.86667 | 22927.188 | 24275.846 | 22927.188 | 26973.162 | 28321.82 | 24275.846 | -13486.581 | -13486.581 | -10789.265 | 228.727 | 229.525 | 231.662 | 49.978
2025-10-21 17:14 | 74176.195 | 83616.805 | -37762.426 | 0.89 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 227.907 | 229.029 | 230.798 | 49.972
2025-10-21 17:15 | 72827.539 | 82268.141 | -37762.426 | 0.89 | 0.88525 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 229.309 | 230.755 | 232.266 | 49.979
2025-10-21 17:16 | 70130.219 | 79570.828 | -37762.426 | 0.88 | 0.88136 | 22927.188 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -13486.581 | -13486.581 | -12137.923 | 228.317 | 229.978 | 231.057 | 49.993
2025-10-21 17:17 | 71478.875 | 80919.484 | -37762.426 | 0.88 | 0.88333 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 228.015 | 229.331 | 230.367 | 49.993
2025-10-21 17:18 | 76873.508 | 87662.773 | -40459.742 | 0.88 | 0.87692 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 29670.479 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 227.41 | 228.77 | 229.849 | 49.985
2025-10-21 17:19 | 75524.852 | 86314.117 | -40459.742 | 0.87 | 0.875 | 25624.504 | 25624.504 | 24275.846 | 29670.479 | 28321.82 | 26973.162 | -14835.239 | -14835.239 | -12137.923 | 228.036 | 229.396 | 230.626 | 50.001
2025-10-21 17:20 | 80919.484 | 93057.406 | -44505.715 | 0.87 | 0.86957 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 228.684 | 229.741 | 231.316 | 50.005
2025-10-21 17:21 | 80919.484 | 93057.406 | -45854.375 | 0.87 | 0.86957 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 228.619 | 229.655 | 231.511 | 49.999
2025-10-21 17:22 | 78222.172 | 91708.75 | -45854.375 | 0.86 | 0.85294 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 228.338 | 229.698 | 231.338 | 49.983
2025-10-21 17:23 | 76873.508 | 87662.773 | -43157.059 | 0.87 | 0.87692 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 227.993 | 229.223 | 230.842 | 49.966
2025-10-21 17:24 | 76873.508 | 89011.43 | -43157.059 | 0.87 | 0.86364 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 228.036 | 228.835 | 230.324 | 49.975
2025-10-21 17:25 | 82268.141 | 93057.406 | -44505.715 | 0.88 | 0.88406 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 228.403 | 229.137 | 230.734 | 49.982
2025-10-21 17:26 | 80919.484 | 93057.406 | -44505.715 | 0.88 | 0.86957 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 228.36 | 229.115 | 230.949 | 49.984
2025-10-21 17:27 | 79570.828 | 91708.75 | -43157.059 | 0.87 | 0.86765 | 28321.82 | 26973.162 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -10789.265 | 228.748 | 229.094 | 231.208 | 49.984
2025-10-21 17:28 | 84965.461 | 97103.383 | -47203.031 | 0.87 | 0.875 | 28321.82 | 29670.479 | 26973.162 | 32367.793 | 35065.109 | 28321.82 | -16183.896 | -17532.555 | -12137.923 | 229.849 | 230.086 | 232.266 | 49.996
2025-10-21 17:29 | 84965.461 | 97103.383 | -45854.375 | 0.88 | 0.875 | 28321.82 | 31019.137 | 26973.162 | 32367.793 | 35065.109 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 229.482 | 230.216 | 232.266 | 50.002
2025-10-21 17:30 | 82268.141 | 93057.406 | -43157.059 | 0.88 | 0.88406 | 26973.162 | 29670.479 | 25624.504 | 31019.137 | 33716.453 | 28321.82 | -14835.239 | -16183.896 | -10789.265 | 229.763 | 230.604 | 232.654 | 49.985
2025-10-21 17:31 | 84965.461 | 97103.383 | -45854.375 | 0.88 | 0.875 | 28321.82 | 29670.479 | 26973.162 | 32367.793 | 33716.453 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 230.302 | 231.144 | 233.021 | 50.005
2025-10-21 17:32 | 74176.195 | 84965.461 | -40459.742 | 0.87 | 0.87302 | 25624.504 | 24275.846 | 22927.188 | 29670.479 | 29670.479 | 25624.504 | -14835.239 | -16183.896 | -10789.265 | 227.475 | 228.166 | 229.741 | 50.036
2025-10-21 17:33 | 80919.484 | 91708.75 | -43157.059 | 0.88 | 0.88235 | 26973.162 | 26973.162 | 25624.504 | 31019.137 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 225.188 | 226.396 | 228.209 | 50.036
2025-10-21 17:34 | 78222.172 | 87662.773 | -37762.426 | 0.9 | 0.89231 | 26973.162 | 25624.504 | 25624.504 | 29670.479 | 29670.479 | 28321.82 | -13486.581 | -13486.581 | -10789.265 | 225.123 | 226.569 | 228.274 | 50.018
2025-10-21 17:35 | 74176.195 | 82268.141 | -35065.109 | 0.9 | 0.90164 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -12137.923 | -10789.265 | 225.468 | 226.569 | 228.187 | 50.016
2025-10-21 17:36 | 72827.539 | 80919.484 | -35065.109 | 0.9 | 0.9 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 25624.504 | -12137.923 | -12137.923 | -9440.606 | 225.296 | 226.526 | 227.864 | 50.016
2025-10-21 17:37 | 74176.195 | 80919.484 | -33716.453 | 0.91 | 0.91667 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 25624.504 | -12137.923 | -12137.923 | -9440.606 | 225.339 | 226.526 | 227.756 | 50.012
2025-10-21 17:38 | 70130.219 | 78222.172 | -33716.453 | 0.9 | 0.89655 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -12137.923 | -12137.923 | -9440.606 | 224.54 | 225.641 | 226.785 | 49.984
2025-10-21 17:39 | 72827.539 | 80919.484 | -33716.453 | 0.9 | 0.9 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 25624.504 | -12137.923 | -12137.923 | -9440.606 | 225.684 | 226.742 | 228.101 | 49.983
2025-10-21 17:40 | 74176.195 | 82268.141 | -35065.109 | 0.9 | 0.90164 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -12137.923 | -12137.923 | -10789.265 | 223.289 | 224.411 | 226.137 | 49.968
2025-10-21 17:41 | 63386.93 | 71478.875 | -31019.137 | 0.9 | 0.88679 | 21578.529 | 21578.529 | 21578.529 | 24275.846 | 24275.846 | 22927.188 | -10789.265 | -10789.265 | -8091.948 | 223.483 | 224.54 | 226.245 | 49.979
2025-10-21 17:42 | 52597.664 | 59340.957 | -28321.82 | 0.88 | 0.88636 | 17532.555 | 17532.555 | 17532.555 | 20229.871 | 20229.871 | 18881.213 | -10789.265 | -9440.606 | -8091.948 | 224.627 | 225.77 | 227.216 | 49.992
2025-10-21 17:43 | 47203.031 | 53946.324 | -25624.504 | 0.88 | 0.875 | 16183.896 | 16183.896 | 16183.896 | 18881.213 | 17532.555 | 17532.555 | -9440.606 | -8091.948 | -6743.291 | 227.13 | 228.425 | 229.504 | 50
2025-10-21 17:44 | 48551.691 | 53946.324 | -22927.188 | 0.9 | 0.9 | 16183.896 | 16183.896 | 16183.896 | 17532.555 | 18881.213 | 17532.555 | -8091.948 | -8091.948 | -6743.291 | 228.252 | 229.676 | 230.237 | 49.998
2025-10-21 17:45 | 45854.375 | 51249.008 | -20229.871 | 0.91 | 0.89474 | 14835.239 | 17532.555 | 14835.239 | 16183.896 | 18881.213 | 16183.896 | -6743.291 | -6743.291 | -6743.291 | 228.597 | 229.612 | 230.518 | 50.005
2025-10-21 17:46 | 48551.691 | 52597.664 | -21578.529 | 0.91 | 0.92308 | 14835.239 | 18881.213 | 14835.239 | 16183.896 | 20229.871 | 16183.896 | -6743.291 | -8091.948 | -6743.291 | 228.274 | 229.504 | 229.892 | 50.027
2025-10-21 17:47 | 48551.691 | 53946.324 | -21578.529 | 0.91 | 0.9 | 14835.239 | 18881.213 | 14835.239 | 16183.896 | 20229.871 | 16183.896 | -6743.291 | -8091.948 | -6743.291 | 228.079 | 229.029 | 229.504 | 50.038
2025-10-21 17:48 | 49900.348 | 55294.98 | -22927.188 | 0.9 | 0.90244 | 14835.239 | 18881.213 | 14835.239 | 17532.555 | 21578.529 | 17532.555 | -8091.948 | -8091.948 | -6743.291 | 228.748 | 230.086 | 229.957 | 50.037
2025-10-21 17:49 | 49900.348 | 55294.98 | -24275.846 | 0.9 | 0.90244 | 14835.239 | 18881.213 | 14835.239 | 17532.555 | 21578.529 | 17532.555 | -8091.948 | -8091.948 | -8091.948 | 229.396 | 230.885 | 231.014 | 50.036
2025-10-21 17:50 | 47203.031 | 51249.008 | -20229.871 | 0.91 | 0.92105 | 14835.239 | 17532.555 | 14835.239 | 16183.896 | 18881.213 | 16183.896 | -6743.291 | -6743.291 | -6743.291 | 227.454 | 228.835 | 229.115 | 50.012
2025-10-21 17:51 | 47203.031 | 51249.008 | -20229.871 | 0.91 | 0.92105 | 14835.239 | 17532.555 | 14835.239 | 16183.896 | 18881.213 | 16183.896 | -6743.291 | -6743.291 | -6743.291 | 226.159 | 227.238 | 227.669 | 49.999
2025-10-21 17:52 | 44505.715 | 48551.691 | -20229.871 | 0.91 | 0.91667 | 14835.239 | 16183.896 | 14835.239 | 16183.896 | 17532.555 | 16183.896 | -6743.291 | -6743.291 | -6743.291 | 226.871 | 228.187 | 228.576 | 49.989
2025-10-21 17:53 | 45854.375 | 49900.348 | -20229.871 | 0.92 | 0.91892 | 14835.239 | 16183.896 | 14835.239 | 16183.896 | 17532.555 | 16183.896 | -6743.291 | -6743.291 | -6743.291 | 225.77 | 227.432 | 227.54 | 49.972
2025-10-21 17:54 | 45854.375 | 49900.348 | -20229.871 | 0.92 | 0.91892 | 14835.239 | 16183.896 | 14835.239 | 16183.896 | 17532.555 | 16183.896 | -6743.291 | -6743.291 | -6743.291 | 225.9 | 227.281 | 227.518 | 49.966
2025-10-21 17:55 | 48551.691 | 53946.324 | -21578.529 | 0.91 | 0.9 | 14835.239 | 18881.213 | 14835.239 | 17532.555 | 20229.871 | 16183.896 | -6743.291 | -8091.948 | -6743.291 | 224.821 | 225.986 | 226.31 | 49.965
2025-10-21 17:56 | 49900.348 | 55294.98 | -22927.188 | 0.9 | 0.90244 | 14835.239 | 18881.213 | 14835.239 | 16183.896 | 21578.529 | 16183.896 | -8091.948 | -8091.948 | -6743.291 | 228.986 | 229.59 | 230.647 | 49.976
2025-10-21 17:57 | 49900.348 | 55294.98 | -22927.188 | 0.9 | 0.90244 | 14835.239 | 18881.213 | 14835.239 | 17532.555 | 21578.529 | 16183.896 | -8091.948 | -8091.948 | -6743.291 | 228.619 | 229.374 | 230.129 | 49.993
2025-10-21 17:58 | 49900.348 | 56643.641 | -24275.846 | 0.89 | 0.88095 | 14835.239 | 20229.871 | 14835.239 | 17532.555 | 21578.529 | 17532.555 | -8091.948 | -9440.606 | -8091.948 | 230.971 | 232.482 | 232.59 | 50.009
2025-10-21 17:59 | 48551.691 | 55294.98 | -24275.846 | 0.89 | 0.87805 | 14835.239 | 18881.213 | 14835.239 | 16183.896 | 21578.529 | 16183.896 | -8091.948 | -9440.606 | -8091.948 | 232.525 | 233.798 | 234.294 | 50.01
2025-10-21 18:00 | 49900.348 | 55294.98 | -25624.504 | 0.89 | 0.90244 | 14835.239 | 18881.213 | 14835.239 | 17532.555 | 21578.529 | 17532.555 | -8091.948 | -9440.606 | -8091.948 | 233.107 | 234.251 | 235.006 | 50.014
2025-10-21 18:01 | 52597.664 | 59340.957 | -26973.162 | 0.89 | 0.88636 | 14835.239 | 21578.529 | 16183.896 | 17532.555 | 22927.188 | 17532.555 | -8091.948 | -9440.606 | -8091.948 | 233.561 | 234.488 | 235.438 | 50.03
2025-10-21 18:02 | 55294.98 | 62038.273 | -26973.162 | 0.89 | 0.8913 | 16183.896 | 21578.529 | 17532.555 | 18881.213 | 22927.188 | 18881.213 | -9440.606 | -9440.606 | -8091.948 | 234.122 | 235.157 | 235.74 | 50.032
2025-10-21 18:03 | 53946.324 | 59340.957 | -26973.162 | 0.89 | 0.90909 | 16183.896 | 20229.871 | 16183.896 | 18881.213 | 22927.188 | 18881.213 | -9440.606 | -9440.606 | -8091.948 | 233.496 | 234.575 | 235.114 | 50.025
2025-10-21 18:04 | 55294.98 | 60689.613 | -26973.162 | 0.9 | 0.91111 | 17532.555 | 20229.871 | 17532.555 | 18881.213 | 22927.188 | 18881.213 | -9440.606 | -9440.606 | -8091.948 | 232.46 | 233.582 | 233.992 | 50.017
2025-10-21 18:05 | 51249.008 | 56643.641 | -24275.846 | 0.9 | 0.90476 | 16183.896 | 18881.213 | 16183.896 | 17532.555 | 21578.529 | 17532.555 | -8091.948 | -8091.948 | -8091.948 | 233.258 | 234.251 | 234.791 | 50.016
2025-10-21 18:06 | 51249.008 | 57992.297 | -25624.504 | 0.89 | 0.88372 | 16183.896 | 18881.213 | 16183.896 | 18881.213 | 21578.529 | 17532.555 | -9440.606 | -9440.606 | -8091.948 | 232.805 | 233.41 | 234.532 | 50.031
2025-10-21 18:07 | 51249.008 | 59340.957 | -28321.82 | 0.88 | 0.86364 | 17532.555 | 17532.555 | 16183.896 | 20229.871 | 20229.871 | 18881.213 | -10789.265 | -9440.606 | -8091.948 | 232.611 | 233.129 | 234.23 | 50.027
2025-10-21 18:08 | 55294.98 | 63386.93 | -29670.479 | 0.88 | 0.87234 | 18881.213 | 18881.213 | 18881.213 | 21578.529 | 21578.529 | 20229.871 | -10789.265 | -10789.265 | -8091.948 | 232.568 | 233.28 | 234.337 | 50.011
2025-10-21 18:09 | 55294.98 | 63386.93 | -31019.137 | 0.87 | 0.87234 | 18881.213 | 18881.213 | 18881.213 | 21578.529 | 21578.529 | 20229.871 | -10789.265 | -10789.265 | -8091.948 | 232.805 | 233.927 | 234.877 | 49.986
2025-10-21 18:10 | 55294.98 | 64735.586 | -32367.793 | 0.86 | 0.85417 | 18881.213 | 18881.213 | 18881.213 | 22927.188 | 21578.529 | 20229.871 | -12137.923 | -10789.265 | -9440.606 | 232.503 | 233.992 | 234.467 | 49.976
2025-10-21 18:11 | 52597.664 | 59340.957 | -28321.82 | 0.88 | 0.88636 | 17532.555 | 17532.555 | 17532.555 | 20229.871 | 20229.871 | 18881.213 | -10789.265 | -9440.606 | -8091.948 | 231.921 | 233.107 | 233.69 | 49.982
2025-10-21 18:12 | 57992.297 | 64735.586 | -29670.479 | 0.88 | 0.89583 | 20229.871 | 18881.213 | 18881.213 | 22927.188 | 21578.529 | 21578.529 | -12137.923 | -10789.265 | -8091.948 | 231.921 | 232.935 | 233.647 | 49.978
2025-10-21 18:13 | 57992.297 | 66084.242 | -31019.137 | 0.88 | 0.87755 | 20229.871 | 18881.213 | 18881.213 | 22927.188 | 21578.529 | 21578.529 | -12137.923 | -10789.265 | -9440.606 | 232.028 | 233.237 | 233.884 | 49.98
2025-10-21 18:14 | 57992.297 | 66084.242 | -29670.479 | 0.88 | 0.87755 | 20229.871 | 18881.213 | 18881.213 | 22927.188 | 21578.529 | 21578.529 | -10789.265 | -10789.265 | -8091.948 | 232.028 | 233.172 | 233.755 | 49.979
2025-10-21 18:15 | 59340.957 | 66084.242 | -31019.137 | 0.88 | 0.89796 | 20229.871 | 18881.213 | 20229.871 | 22927.188 | 21578.529 | 21578.529 | -12137.923 | -10789.265 | -8091.948 | 232.244 | 232.978 | 233.906 | 49.982
2025-10-21 18:16 | 57992.297 | 66084.242 | -31019.137 | 0.88 | 0.87755 | 20229.871 | 18881.213 | 20229.871 | 22927.188 | 21578.529 | 21578.529 | -12137.923 | -10789.265 | -8091.948 | 231.662 | 232.654 | 233.474 | 49.996
2025-10-21 18:17 | 57992.297 | 67432.906 | -32367.793 | 0.87 | 0.86 | 20229.871 | 18881.213 | 18881.213 | 22927.188 | 22927.188 | 21578.529 | -12137.923 | -10789.265 | -9440.606 | 232.633 | 234.1 | 234.424 | 50.011
2025-10-21 18:18 | 57992.297 | 66084.242 | -32367.793 | 0.87 | 0.87755 | 20229.871 | 18881.213 | 18881.213 | 22927.188 | 21578.529 | 21578.529 | -12137.923 | -10789.265 | -9440.606 | 232.331 | 233.561 | 233.971 | 50.008
2025-10-21 18:19 | 60689.613 | 68781.563 | -32367.793 | 0.88 | 0.88235 | 20229.871 | 20229.871 | 20229.871 | 24275.846 | 22927.188 | 21578.529 | -12137.923 | -10789.265 | -9440.606 | 231.942 | 232.719 | 233.345 | 50.008
2025-10-21 18:20 | 57992.297 | 64735.586 | -29670.479 | 0.88 | 0.89583 | 20229.871 | 18881.213 | 18881.213 | 22927.188 | 21578.529 | 21578.529 | -10789.265 | -10789.265 | -8091.948 | 232.633 | 233.582 | 234.078 | 50.003
2025-10-21 18:21 | 60689.613 | 68781.563 | -32367.793 | 0.88 | 0.88235 | 20229.871 | 20229.871 | 20229.871 | 24275.846 | 22927.188 | 21578.529 | -12137.923 | -10789.265 | -9440.606 | 232.158 | 232.913 | 233.431 | 49.991
2025-10-21 18:22 | 60689.613 | 68781.563 | -32367.793 | 0.88 | 0.88235 | 20229.871 | 20229.871 | 20229.871 | 24275.846 | 24275.846 | 21578.529 | -12137.923 | -12137.923 | -8091.948 | 231.726 | 231.985 | 233.388 | 49.974
2025-10-21 18:23 | 62038.273 | 70130.219 | -32367.793 | 0.89 | 0.88462 | 20229.871 | 21578.529 | 20229.871 | 24275.846 | 24275.846 | 21578.529 | -12137.923 | -12137.923 | -8091.948 | 231.575 | 231.964 | 233.431 | 49.982
2025-10-21 18:24 | 62038.273 | 70130.219 | -33716.453 | 0.88 | 0.88462 | 20229.871 | 21578.529 | 20229.871 | 24275.846 | 24275.846 | 21578.529 | -12137.923 | -12137.923 | -9440.606 | 232.546 | 233.28 | 234.488 | 49.973
2025-10-21 18:25 | 59340.957 | 68781.563 | -32367.793 | 0.87 | 0.86275 | 20229.871 | 21578.529 | 18881.213 | 22927.188 | 24275.846 | 20229.871 | -12137.923 | -12137.923 | -9440.606 | 232.719 | 233.086 | 234.64 | 49.97
2025-10-21 18:26 | 62038.273 | 71478.875 | -35065.109 | 0.87 | 0.86792 | 20229.871 | 24275.846 | 18881.213 | 22927.188 | 26973.162 | 21578.529 | -12137.923 | -13486.581 | -9440.606 | 232.395 | 232.848 | 234.64 | 49.975
2025-10-21 18:27 | 59340.957 | 67432.906 | -32367.793 | 0.87 | 0.88 | 18881.213 | 22927.188 | 17532.555 | 21578.529 | 25624.504 | 20229.871 | -10789.265 | -13486.581 | -8091.948 | 232.978 | 233.41 | 235.179 | 49.964
2025-10-21 18:28 | 60689.613 | 70130.219 | -35065.109 | 0.86 | 0.86538 | 20229.871 | 21578.529 | 18881.213 | 22927.188 | 25624.504 | 21578.529 | -12137.923 | -13486.581 | -9440.606 | 232.827 | 233.021 | 234.877 | 49.978
2025-10-21 18:29 | 62038.273 | 70130.219 | -32367.793 | 0.88 | 0.88462 | 20229.871 | 21578.529 | 18881.213 | 22927.188 | 25624.504 | 21578.529 | -12137.923 | -12137.923 | -8091.948 | 231.014 | 230.863 | 233.043 | 49.978
2025-10-21 18:30 | 60689.613 | 70130.219 | -33716.453 | 0.87 | 0.86538 | 20229.871 | 21578.529 | 18881.213 | 22927.188 | 24275.846 | 21578.529 | -12137.923 | -12137.923 | -9440.606 | 231.273 | 230.863 | 232.913 | 49.979
2025-10-21 18:31 | 62038.273 | 70130.219 | -32367.793 | 0.88 | 0.88462 | 20229.871 | 21578.529 | 18881.213 | 22927.188 | 25624.504 | 21578.529 | -12137.923 | -12137.923 | -8091.948 | 229.935 | 229.633 | 231.64 | 49.995
2025-10-21 18:32 | 60689.613 | 68781.563 | -32367.793 | 0.88 | 0.88235 | 20229.871 | 21578.529 | 18881.213 | 22927.188 | 25624.504 | 21578.529 | -10789.265 | -12137.923 | -8091.948 | 229.051 | 229.007 | 230.928 | 50.014
2025-10-21 18:33 | 62038.273 | 70130.219 | -32367.793 | 0.88 | 0.88462 | 20229.871 | 21578.529 | 20229.871 | 24275.846 | 24275.846 | 21578.529 | -12137.923 | -12137.923 | -9440.606 | 230.043 | 230.518 | 231.834 | 50.015
2025-10-21 18:34 | 63386.93 | 71478.875 | -33716.453 | 0.88 | 0.88679 | 21578.529 | 21578.529 | 20229.871 | 24275.846 | 24275.846 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 228.187 | 228.835 | 229.914 | 50.021
2025-10-21 18:35 | 57992.297 | 66084.242 | -31019.137 | 0.88 | 0.87755 | 20229.871 | 20229.871 | 18881.213 | 22927.188 | 22927.188 | 21578.529 | -10789.265 | -10789.265 | -9440.606 | 229.029 | 229.482 | 230.496 | 50.014
2025-10-21 18:36 | 62038.273 | 70130.219 | -32367.793 | 0.88 | 0.88462 | 21578.529 | 21578.529 | 20229.871 | 24275.846 | 24275.846 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 229.18 | 229.525 | 230.842 | 50.023
2025-10-21 18:37 | 70130.219 | 80919.484 | -39111.086 | 0.87 | 0.86667 | 24275.846 | 22927.188 | 22927.188 | 28321.82 | 26973.162 | 24275.846 | -13486.581 | -14835.239 | -10789.265 | 228.079 | 228.533 | 230.216 | 50.019
2025-10-21 18:38 | 67432.906 | 78222.172 | -37762.426 | 0.87 | 0.86207 | 24275.846 | 21578.529 | 21578.529 | 26973.162 | 25624.504 | 24275.846 | -13486.581 | -14835.239 | -9440.606 | 227.022 | 227.777 | 229.029 | 50.015
2025-10-21 18:39 | 67432.906 | 79570.828 | -40459.742 | 0.85 | 0.84746 | 24275.846 | 21578.529 | 21578.529 | 28321.82 | 26973.162 | 24275.846 | -14835.239 | -14835.239 | -10789.265 | 227.972 | 229.051 | 230.302 | 49.995
2025-10-21 18:40 | 74176.195 | 86314.117 | -44505.715 | 0.86 | 0.85938 | 25624.504 | 24275.846 | 24275.846 | 31019.137 | 29670.479 | 26973.162 | -16183.896 | -16183.896 | -12137.923 | 227.756 | 228.705 | 230.022 | 49.979
2025-10-21 18:41 | 72827.539 | 86314.117 | -44505.715 | 0.85 | 0.84375 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 28321.82 | 26973.162 | -16183.896 | -16183.896 | -12137.923 | 228.468 | 229.331 | 230.604 | 49.975
2025-10-21 18:42 | 75524.852 | 87662.773 | -41808.402 | 0.87 | 0.86154 | 25624.504 | 25624.504 | 24275.846 | 29670.479 | 29670.479 | 26973.162 | -14835.239 | -14835.239 | -12137.923 | 228.489 | 229.051 | 230.539 | 49.976
2025-10-21 18:43 | 76873.508 | 87662.773 | -41808.402 | 0.88 | 0.87692 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 227.799 | 228.705 | 229.849 | 49.978
2025-10-21 18:44 | 82268.141 | 93057.406 | -44505.715 | 0.88 | 0.88406 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 227.389 | 228.274 | 229.547 | 49.993
2025-10-21 18:45 | 76873.508 | 89011.43 | -44505.715 | 0.87 | 0.86364 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 228.317 | 229.396 | 230.561 | 50.014
2025-10-21 18:46 | 80919.484 | 91708.75 | -43157.059 | 0.88 | 0.88235 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 227.626 | 228.964 | 230.237 | 50.026
2025-10-21 18:47 | 82268.141 | 94406.063 | -47203.031 | 0.86 | 0.87143 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 31019.137 | -17532.555 | -16183.896 | -13486.581 | 227.691 | 228.662 | 229.698 | 50.008
2025-10-21 18:48 | 84965.461 | 97103.383 | -45854.375 | 0.88 | 0.875 | 29670.479 | 26973.162 | 28321.82 | 35065.109 | 31019.137 | 31019.137 | -17532.555 | -16183.896 | -13486.581 | 227.648 | 228.921 | 229.849 | 50.007
2025-10-21 18:49 | 87662.773 | 99800.695 | -47203.031 | 0.88 | 0.87838 | 31019.137 | 26973.162 | 29670.479 | 35065.109 | 32367.793 | 32367.793 | -17532.555 | -16183.896 | -13486.581 | 227.562 | 228.899 | 230 | 50.007
2025-10-21 18:50 | 80919.484 | 94406.063 | -45854.375 | 0.87 | 0.85714 | 28321.82 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -17532.555 | -16183.896 | -13486.581 | 227.842 | 228.856 | 230 | 50.002
2025-10-21 18:51 | 79570.828 | 90360.094 | -41808.402 | 0.88 | 0.8806 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 28321.82 | 29670.479 | -14835.239 | -14835.239 | -12137.923 | 227.303 | 228.533 | 229.353 | 49.992
2025-10-21 18:52 | 76873.508 | 90360.094 | -45854.375 | 0.86 | 0.85075 | 26973.162 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 227.475 | 228.684 | 229.914 | 49.993
2025-10-21 18:53 | 79570.828 | 91708.75 | -44505.715 | 0.87 | 0.86765 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 28321.82 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 227.238 | 228.274 | 229.698 | 49.992
2025-10-21 18:54 | 82268.141 | 93057.406 | -44505.715 | 0.88 | 0.88406 | 29670.479 | 25624.504 | 28321.82 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 227.454 | 228.446 | 229.784 | 49.984
2025-10-21 18:55 | 79570.828 | 90360.094 | -43157.059 | 0.87 | 0.8806 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 28321.82 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 227.346 | 228.252 | 229.849 | 49.978
2025-10-21 18:56 | 82268.141 | 94406.063 | -44505.715 | 0.87 | 0.87143 | 28321.82 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 227.022 | 227.777 | 229.784 | 49.988
2025-10-21 18:57 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 28321.82 | 26973.162 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 227.454 | 228.382 | 230.108 | 49.991
2025-10-21 18:58 | 76873.508 | 89011.43 | -44505.715 | 0.86 | 0.86364 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 227.82 | 229.007 | 230.41 | 49.985
2025-10-21 18:59 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 227.367 | 228.533 | 229.978 | 49.995
2025-10-21 19:00 | 78222.172 | 90360.094 | -43157.059 | 0.87 | 0.86567 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -10789.265 | 227.367 | 228.403 | 229.935 | 50.019
2025-10-21 19:01 | 82268.141 | 93057.406 | -44505.715 | 0.87 | 0.88406 | 28321.82 | 26973.162 | 25624.504 | 32367.793 | 32367.793 | 28321.82 | -16183.896 | -17532.555 | -12137.923 | 226.245 | 227.648 | 228.835 | 50.022
2025-10-21 19:02 | 78222.172 | 90360.094 | -44505.715 | 0.87 | 0.86567 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 31019.137 | 26973.162 | -14835.239 | -17532.555 | -12137.923 | 225.145 | 226.547 | 227.734 | 50.01
2025-10-21 19:03 | 74176.195 | 86314.117 | -43157.059 | 0.86 | 0.85938 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 29670.479 | 26973.162 | -14835.239 | -17532.555 | -12137.923 | 224.864 | 226.116 | 227.389 | 50.021
2025-10-21 19:04 | 75524.852 | 86314.117 | -41808.402 | 0.87 | 0.875 | 25624.504 | 25624.504 | 24275.846 | 29670.479 | 29670.479 | 26973.162 | -14835.239 | -16183.896 | -12137.923 | 225.274 | 226.353 | 227.713 | 50.018
2025-10-21 19:05 | 71478.875 | 80919.484 | -36413.77 | 0.89 | 0.88333 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 28321.82 | 25624.504 | -12137.923 | -13486.581 | -10789.265 | 225.576 | 226.677 | 227.993 | 50.017
2025-10-21 19:06 | 72827.539 | 82268.141 | -37762.426 | 0.89 | 0.88525 | 24275.846 | 25624.504 | 22927.188 | 26973.162 | 28321.82 | 25624.504 | -12137.923 | -13486.581 | -10789.265 | 225.274 | 226.526 | 227.842 | 50.002
2025-10-21 19:07 | 71478.875 | 79570.828 | -36413.77 | 0.89 | 0.89831 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -12137.923 | -13486.581 | -10789.265 | 225.188 | 226.526 | 227.713 | 49.996
2025-10-21 19:08 | 71478.875 | 80919.484 | -37762.426 | 0.88 | 0.88333 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 25624.504 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 225.555 | 226.439 | 228.015 | 49.998
2025-10-21 19:09 | 66084.242 | 74176.195 | -33716.453 | 0.88 | 0.89091 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 225.231 | 225.641 | 227.454 | 49.996
2025-10-21 19:10 | 74176.195 | 84965.461 | -39111.086 | 0.88 | 0.87302 | 25624.504 | 24275.846 | 25624.504 | 29670.479 | 26973.162 | 28321.82 | -13486.581 | -13486.581 | -12137.923 | 224.67 | 225.253 | 227 | 49.993
2025-10-21 19:11 | 70130.219 | 79570.828 | -36413.77 | 0.89 | 0.88136 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 225.209 | 226.073 | 227.432 | 50.004
2025-10-21 19:12 | 71478.875 | 79570.828 | -35065.109 | 0.89 | 0.89831 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 225.231 | 226.029 | 227.756 | 50
2025-10-21 19:13 | 71478.875 | 80919.484 | -36413.77 | 0.89 | 0.88333 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -12137.923 | -13486.581 | -10789.265 | 225.296 | 226.008 | 227.842 | 50.012
2025-10-21 19:14 | 68781.563 | 76873.508 | -35065.109 | 0.89 | 0.89474 | 22927.188 | 22927.188 | 21578.529 | 25624.504 | 25624.504 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 225.145 | 225.943 | 227.54 | 50.017
2025-10-21 19:15 | 72827.539 | 80919.484 | -35065.109 | 0.9 | 0.9 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 225.123 | 225.965 | 227.54 | 50.018
2025-10-21 19:16 | 70130.219 | 79570.828 | -35065.109 | 0.9 | 0.88136 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -12137.923 | -12137.923 | -9440.606 | 225.425 | 225.512 | 227.238 | 50.009
2025-10-21 19:17 | 72827.539 | 80919.484 | -35065.109 | 0.9 | 0.9 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 25624.504 | -12137.923 | -12137.923 | -9440.606 | 224.972 | 225.576 | 227.087 | 49.989
2025-10-21 19:18 | 67432.906 | 75524.852 | -33716.453 | 0.89 | 0.89286 | 22927.188 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 224.692 | 225.317 | 226.785 | 49.985
2025-10-21 19:19 | 70130.219 | 80919.484 | -37762.426 | 0.88 | 0.86667 | 24275.846 | 21578.529 | 24275.846 | 28321.82 | 25624.504 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 226.483 | 226.957 | 228.576 | 49.977
2025-10-21 19:20 | 67432.906 | 75524.852 | -35065.109 | 0.89 | 0.89286 | 22927.188 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 227.648 | 228.619 | 229.655 | 49.986
2025-10-21 19:21 | 68781.563 | 78222.172 | -36413.77 | 0.88 | 0.87931 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 227.885 | 228.684 | 230.043 | 49.986
2025-10-21 19:22 | 68781.563 | 78222.172 | -36413.77 | 0.88 | 0.87931 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 227.842 | 228.489 | 230.043 | 49.992
2025-10-21 19:23 | 67432.906 | 76873.508 | -36413.77 | 0.88 | 0.87719 | 22927.188 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 24275.846 | -13486.581 | -12137.923 | -10789.265 | 228.554 | 229.094 | 230.604 | 50.004
2025-10-21 19:24 | 72827.539 | 82268.141 | -39111.086 | 0.88 | 0.88525 | 25624.504 | 22927.188 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 228.252 | 228.338 | 230.022 | 50.014
2025-10-21 19:25 | 70130.219 | 79570.828 | -37762.426 | 0.88 | 0.88136 | 24275.846 | 21578.529 | 22927.188 | 28321.82 | 25624.504 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 227.993 | 228.576 | 229.914 | 50.01
2025-10-21 19:26 | 71478.875 | 82268.141 | -39111.086 | 0.88 | 0.86885 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 226.957 | 227.842 | 229.266 | 50.014
2025-10-21 19:27 | 67432.906 | 76873.508 | -35065.109 | 0.89 | 0.87719 | 22927.188 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 227.346 | 227.842 | 229.202 | 50.006
2025-10-21 19:28 | 70130.219 | 79570.828 | -36413.77 | 0.88 | 0.88136 | 24275.846 | 21578.529 | 22927.188 | 28321.82 | 25624.504 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 227.41 | 227.95 | 229.029 | 50.017
2025-10-21 19:29 | 67432.906 | 76873.508 | -37762.426 | 0.87 | 0.87719 | 22927.188 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 226.439 | 227.281 | 228.36 | 50.017
2025-10-21 19:30 | 74176.195 | 83616.805 | -37762.426 | 0.89 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 227.389 | 228.144 | 229.547 | 50.007
2025-10-21 19:31 | 76873.508 | 86314.117 | -40459.742 | 0.88 | 0.89062 | 25624.504 | 26973.162 | 24275.846 | 28321.82 | 31019.137 | 26973.162 | -13486.581 | -14835.239 | -10789.265 | 227.324 | 228.079 | 229.978 | 49.994
2025-10-21 19:32 | 72827.539 | 83616.805 | -39111.086 | 0.88 | 0.87097 | 24275.846 | 25624.504 | 22927.188 | 26973.162 | 29670.479 | 25624.504 | -13486.581 | -14835.239 | -10789.265 | 226.893 | 227.346 | 229.547 | 50.009
2025-10-21 19:33 | 76873.508 | 87662.773 | -40459.742 | 0.88 | 0.87692 | 25624.504 | 26973.162 | 24275.846 | 29670.479 | 31019.137 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 227.259 | 227.756 | 230.022 | 50.002
2025-10-21 19:34 | 78222.172 | 87662.773 | -40459.742 | 0.88 | 0.89231 | 25624.504 | 26973.162 | 24275.846 | 29670.479 | 31019.137 | 26973.162 | -13486.581 | -14835.239 | -10789.265 | 227.885 | 228.36 | 230.561 | 50.006
2025-10-21 19:35 | 74176.195 | 84965.461 | -40459.742 | 0.88 | 0.87302 | 24275.846 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -13486.581 | -14835.239 | -10789.265 | 228.101 | 228.295 | 230.583 | 50.001
2025-10-21 19:36 | 68781.563 | 78222.172 | -37762.426 | 0.87 | 0.87931 | 22927.188 | 22927.188 | 22927.188 | 26973.162 | 26973.162 | 24275.846 | -13486.581 | -13486.581 | -10789.265 | 228.058 | 228.36 | 230.237 | 50.003
2025-10-21 19:37 | 66084.242 | 75524.852 | -36413.77 | 0.87 | 0.875 | 22927.188 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 24275.846 | -13486.581 | -12137.923 | -10789.265 | 227.044 | 228.23 | 229.223 | 49.998
2025-10-21 19:38 | 72827.539 | 82268.141 | -37762.426 | 0.88 | 0.88525 | 25624.504 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 227.173 | 228.274 | 229.288 | 50.007
2025-10-21 19:39 | 71478.875 | 80919.484 | -37762.426 | 0.89 | 0.88333 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 25624.504 | 26973.162 | -13486.581 | -12137.923 | -10789.265 | 227.41 | 228.446 | 229.612 | 50.009
2025-10-21 19:40 | 71478.875 | 80919.484 | -39111.086 | 0.87 | 0.88333 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 25624.504 | 26973.162 | -14835.239 | -13486.581 | -12137.923 | 227.087 | 227.95 | 229.202 | 50.019
2025-10-21 19:41 | 74176.195 | 84965.461 | -40459.742 | 0.88 | 0.87302 | 25624.504 | 22927.188 | 25624.504 | 29670.479 | 26973.162 | 28321.82 | -14835.239 | -13486.581 | -12137.923 | 227.669 | 228.684 | 230 | 50.018
2025-10-21 19:42 | 71478.875 | 80919.484 | -37762.426 | 0.88 | 0.88333 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 227.669 | 228.899 | 230.432 | 50.017
2025-10-21 19:43 | 71478.875 | 80919.484 | -37762.426 | 0.88 | 0.88333 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 227.82 | 228.964 | 230.475 | 50.016
2025-10-21 19:44 | 71478.875 | 80919.484 | -37762.426 | 0.88 | 0.88333 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 25624.504 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 228.23 | 229.353 | 230.777 | 50.016
2025-10-21 19:45 | 66084.242 | 75524.852 | -36413.77 | 0.88 | 0.875 | 22927.188 | 21578.529 | 21578.529 | 26973.162 | 24275.846 | 24275.846 | -13486.581 | -12137.923 | -10789.265 | 227.82 | 228.856 | 230.453 | 50.021
2025-10-21 19:46 | 64735.586 | 74176.195 | -36413.77 | 0.87 | 0.87273 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -13486.581 | -12137.923 | -10789.265 | 228.187 | 229.094 | 230.777 | 49.994
2025-10-21 19:47 | 71478.875 | 80919.484 | -39111.086 | 0.87 | 0.88333 | 24275.846 | 24275.846 | 22927.188 | 28321.82 | 26973.162 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 227.389 | 227.928 | 230.151 | 49.975
2025-10-21 19:48 | 75524.852 | 86314.117 | -40459.742 | 0.88 | 0.875 | 25624.504 | 25624.504 | 24275.846 | 29670.479 | 29670.479 | 26973.162 | -14835.239 | -14835.239 | -12137.923 | 227.993 | 228.856 | 230.949 | 49.985
2025-10-21 19:49 | 71478.875 | 79570.828 | -36413.77 | 0.89 | 0.89831 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -12137.923 | -13486.581 | -10789.265 | 228.403 | 229.396 | 231.381 | 49.986
2025-10-21 19:50 | 72827.539 | 82268.141 | -37762.426 | 0.89 | 0.88525 | 24275.846 | 24275.846 | 22927.188 | 28321.82 | 28321.82 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 225.663 | 226.742 | 228.511 | 49.975
2025-10-21 19:51 | 71478.875 | 79570.828 | -35065.109 | 0.9 | 0.89831 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 224.54 | 225.706 | 227.324 | 49.983
2025-10-21 19:52 | 68781.563 | 76873.508 | -35065.109 | 0.89 | 0.89474 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 225.36 | 226.655 | 228.058 | 49.986
2025-10-21 19:53 | 68781.563 | 78222.172 | -36413.77 | 0.89 | 0.87931 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 225.317 | 226.698 | 228.079 | 50.004
2025-10-21 19:54 | 68781.563 | 76873.508 | -35065.109 | 0.89 | 0.89474 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 25624.504 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 225.339 | 226.612 | 227.95 | 49.996
2025-10-21 19:55 | 64735.586 | 72827.539 | -33716.453 | 0.88 | 0.88889 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 24275.846 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 225.598 | 226.59 | 227.95 | 49.997
2025-10-21 19:56 | 63386.93 | 72827.539 | -33716.453 | 0.88 | 0.87037 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 225.684 | 226.31 | 227.799 | 50.017
2025-10-21 19:57 | 63386.93 | 71478.875 | -33716.453 | 0.89 | 0.88679 | 21578.529 | 20229.871 | 21578.529 | 24275.846 | 24275.846 | 22927.188 | -10789.265 | -12137.923 | -10789.265 | 226.375 | 227.95 | 228.641 | 50.019
2025-10-21 19:58 | 66084.242 | 74176.195 | -32367.793 | 0.9 | 0.89091 | 21578.529 | 24275.846 | 21578.529 | 24275.846 | 26973.162 | 22927.188 | -10789.265 | -12137.923 | -9440.606 | 226.418 | 227.691 | 228.705 | 50.022
2025-10-21 19:59 | 72827.539 | 82268.141 | -37762.426 | 0.89 | 0.88525 | 24275.846 | 25624.504 | 22927.188 | 28321.82 | 28321.82 | 25624.504 | -12137.923 | -13486.581 | -10789.265 | 226.332 | 227.54 | 228.835 | 50.01
2025-10-21 20:00 | 72827.539 | 80919.484 | -35065.109 | 0.9 | 0.9 | 24275.846 | 25624.504 | 22927.188 | 26973.162 | 28321.82 | 24275.846 | -12137.923 | -13486.581 | -9440.606 | 227.216 | 228.295 | 229.849 | 50.011
2025-10-21 20:01 | 75524.852 | 83616.805 | -37762.426 | 0.89 | 0.90323 | 24275.846 | 26973.162 | 24275.846 | 28321.82 | 29670.479 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 225.663 | 226.353 | 228.36 | 49.98
2025-10-21 20:02 | 72827.539 | 80919.484 | -36413.77 | 0.89 | 0.9 | 24275.846 | 25624.504 | 22927.188 | 26973.162 | 28321.82 | 25624.504 | -13486.581 | -13486.581 | -9440.606 | 225.037 | 225.015 | 227.734 | 49.926
2025-10-21 20:03 | 76873.508 | 86314.117 | -39111.086 | 0.89 | 0.89062 | 25624.504 | 26973.162 | 24275.846 | 28321.82 | 31019.137 | 26973.162 | -13486.581 | -14835.239 | -10789.265 | 225.36 | 225.49 | 227.95 | 49.925
2025-10-21 20:04 | 71478.875 | 79570.828 | -35065.109 | 0.9 | 0.89831 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 225.339 | 226.634 | 227.82 | 49.941
2025-10-21 20:05 | 72827.539 | 80919.484 | -35065.109 | 0.9 | 0.9 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 224.972 | 226.073 | 227.432 | 49.976
2025-10-21 20:06 | 75524.852 | 84965.461 | -36413.77 | 0.9 | 0.88889 | 25624.504 | 26973.162 | 24275.846 | 28321.82 | 29670.479 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 225.123 | 225.814 | 227.454 | 49.977
2025-10-21 20:07 | 71478.875 | 80919.484 | -35065.109 | 0.89 | 0.88333 | 24275.846 | 25624.504 | 22927.188 | 26973.162 | 28321.82 | 24275.846 | -12137.923 | -13486.581 | -9440.606 | 225.598 | 226.569 | 227.756 | 49.987
2025-10-21 20:08 | 74176.195 | 82268.141 | -36413.77 | 0.9 | 0.90164 | 24275.846 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 225.512 | 226.698 | 228.036 | 49.998
2025-10-21 20:09 | 75524.852 | 83616.805 | -36413.77 | 0.9 | 0.90323 | 24275.846 | 26973.162 | 24275.846 | 28321.82 | 29670.479 | 25624.504 | -12137.923 | -13486.581 | -10789.265 | 225.684 | 226.914 | 228.23 | 49.996
2025-10-21 20:10 | 78222.172 | 86314.117 | -37762.426 | 0.9 | 0.90625 | 25624.504 | 26973.162 | 24275.846 | 29670.479 | 31019.137 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 225.339 | 226.353 | 227.756 | 50.005
2025-10-21 20:11 | 74176.195 | 83616.805 | -36413.77 | 0.9 | 0.8871 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -12137.923 | -10789.265 | 225.684 | 226.073 | 227.907 | 49.998
2025-10-21 20:12 | 72827.539 | 80919.484 | -36413.77 | 0.89 | 0.9 | 24275.846 | 24275.846 | 22927.188 | 28321.82 | 26973.162 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 225.209 | 226.224 | 227.432 | 50.013
2025-10-21 20:13 | 67432.906 | 75524.852 | -33716.453 | 0.89 | 0.89286 | 22927.188 | 22927.188 | 21578.529 | 25624.504 | 25624.504 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 225.684 | 227.065 | 228.187 | 50.019
2025-10-21 20:14 | 72827.539 | 80919.484 | -35065.109 | 0.9 | 0.9 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 225.943 | 226.742 | 228.166 | 50.019
2025-10-21 20:15 | 72827.539 | 80919.484 | -35065.109 | 0.9 | 0.9 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 226.461 | 227.173 | 228.576 | 49.998
2025-10-21 20:16 | 72827.539 | 80919.484 | -36413.77 | 0.89 | 0.9 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 226.353 | 227.108 | 228.425 | 49.98
2025-10-21 20:17 | 74176.195 | 83616.805 | -37762.426 | 0.89 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 226.806 | 227.562 | 229.051 | 49.98
2025-10-21 20:18 | 72827.539 | 82268.141 | -37762.426 | 0.89 | 0.88525 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 226.785 | 227.626 | 229.115 | 50
2025-10-21 20:19 | 72827.539 | 82268.141 | -37762.426 | 0.89 | 0.88525 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 226.742 | 227.454 | 229.288 | 50.006
2025-10-21 20:20 | 72827.539 | 80919.484 | -36413.77 | 0.89 | 0.9 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 226.72 | 227.108 | 229.18 | 50.012
2025-10-21 20:21 | 76873.508 | 86314.117 | -39111.086 | 0.89 | 0.89062 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 28321.82 | 26973.162 | -14835.239 | -13486.581 | -10789.265 | 226.849 | 227.303 | 229.309 | 50.015
2025-10-21 20:22 | 72827.539 | 80919.484 | -35065.109 | 0.9 | 0.9 | 24275.846 | 25624.504 | 22927.188 | 26973.162 | 28321.82 | 25624.504 | -12137.923 | -12137.923 | -9440.606 | 226.914 | 227.087 | 229.331 | 50.011
2025-10-21 20:23 | 74176.195 | 83616.805 | -36413.77 | 0.9 | 0.8871 | 24275.846 | 25624.504 | 24275.846 | 28321.82 | 28321.82 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 226.526 | 226.461 | 228.835 | 50.014
2025-10-21 20:24 | 70130.219 | 79570.828 | -36413.77 | 0.88 | 0.88136 | 22927.188 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 24275.846 | -13486.581 | -13486.581 | -9440.606 | 226.439 | 225.986 | 228.792 | 50.029
2025-10-21 20:25 | 74176.195 | 83616.805 | -36413.77 | 0.9 | 0.8871 | 24275.846 | 25624.504 | 24275.846 | 28321.82 | 28321.82 | 25624.504 | -13486.581 | -13486.581 | -9440.606 | 227.065 | 226.59 | 229.547 | 50.03
2025-10-21 20:26 | 72827.539 | 80919.484 | -35065.109 | 0.9 | 0.9 | 24275.846 | 25624.504 | 22927.188 | 26973.162 | 28321.82 | 25624.504 | -12137.923 | -12137.923 | -9440.606 | 226.418 | 226.612 | 229.094 | 50.032
2025-10-21 20:27 | 72827.539 | 80919.484 | -35065.109 | 0.9 | 0.9 | 24275.846 | 25624.504 | 22927.188 | 26973.162 | 28321.82 | 25624.504 | -12137.923 | -12137.923 | -9440.606 | 226.893 | 226.957 | 229.245 | 50.023
2025-10-21 20:28 | 72827.539 | 80919.484 | -35065.109 | 0.9 | 0.9 | 24275.846 | 25624.504 | 22927.188 | 26973.162 | 28321.82 | 25624.504 | -12137.923 | -13486.581 | -9440.606 | 227.475 | 227.152 | 229.698 | 50.015
2025-10-21 20:29 | 68781.563 | 76873.508 | -33716.453 | 0.89 | 0.89474 | 22927.188 | 24275.846 | 21578.529 | 25624.504 | 26973.162 | 24275.846 | -12137.923 | -13486.581 | -9440.606 | 226.936 | 226.677 | 229.115 | 50.01
2025-10-21 20:30 | 71478.875 | 79570.828 | -35065.109 | 0.89 | 0.89831 | 22927.188 | 25624.504 | 22927.188 | 26973.162 | 28321.82 | 24275.846 | -12137.923 | -13486.581 | -9440.606 | 227.13 | 227.108 | 229.396 | 50.007
2025-10-21 20:31 | 70130.219 | 76873.508 | -33716.453 | 0.9 | 0.91228 | 22927.188 | 24275.846 | 21578.529 | 25624.504 | 28321.82 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 228.209 | 228.295 | 230.561 | 49.987
2025-10-21 20:32 | 70130.219 | 79570.828 | -36413.77 | 0.89 | 0.88136 | 22927.188 | 24275.846 | 21578.529 | 26973.162 | 28321.82 | 24275.846 | -13486.581 | -13486.581 | -9440.606 | 228.382 | 228.187 | 230.755 | 49.954
2025-10-21 20:33 | 68781.563 | 78222.172 | -36413.77 | 0.88 | 0.87931 | 22927.188 | 24275.846 | 21578.529 | 25624.504 | 28321.82 | 24275.846 | -13486.581 | -13486.581 | -9440.606 | 228.533 | 228.382 | 230.626 | 49.964
2025-10-21 20:34 | 71478.875 | 79570.828 | -35065.109 | 0.9 | 0.89831 | 24275.846 | 25624.504 | 22927.188 | 26973.162 | 28321.82 | 24275.846 | -12137.923 | -13486.581 | -9440.606 | 227.626 | 227.367 | 229.59 | 49.972
2025-10-21 20:35 | 71478.875 | 79570.828 | -35065.109 | 0.9 | 0.89831 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -12137.923 | -12137.923 | -9440.606 | 228.382 | 228.684 | 229.978 | 49.98
2025-10-21 20:36 | 70130.219 | 79570.828 | -36413.77 | 0.89 | 0.88136 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 227.993 | 228.36 | 229.568 | 50.009
2025-10-21 20:37 | 68781.563 | 76873.508 | -33716.453 | 0.9 | 0.89474 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 227.713 | 228.23 | 229.676 | 50.014
2025-10-21 20:38 | 71478.875 | 79570.828 | -33716.453 | 0.9 | 0.89831 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -12137.923 | -12137.923 | -9440.606 | 227.432 | 228.123 | 229.266 | 50.013
2025-10-21 20:39 | 70130.219 | 79570.828 | -35065.109 | 0.89 | 0.88136 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 227.972 | 228.425 | 229.655 | 50.022
2025-10-21 20:40 | 74176.195 | 83616.805 | -36413.77 | 0.9 | 0.8871 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 28321.82 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 227.044 | 227.54 | 228.899 | 50.032
2025-10-21 20:41 | 72827.539 | 80919.484 | -35065.109 | 0.89 | 0.9 | 24275.846 | 25624.504 | 22927.188 | 26973.162 | 28321.82 | 25624.504 | -12137.923 | -13486.581 | -9440.606 | 227.864 | 228.187 | 229.892 | 50.023
2025-10-21 20:42 | 71478.875 | 80919.484 | -36413.77 | 0.89 | 0.88333 | 22927.188 | 25624.504 | 22927.188 | 26973.162 | 28321.82 | 24275.846 | -12137.923 | -13486.581 | -10789.265 | 227.734 | 228.641 | 230.194 | 50.013
2025-10-21 20:43 | 71478.875 | 79570.828 | -35065.109 | 0.9 | 0.89831 | 24275.846 | 25624.504 | 22927.188 | 26973.162 | 28321.82 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 228.079 | 228.964 | 230.432 | 50.009
2025-10-21 20:44 | 71478.875 | 80919.484 | -35065.109 | 0.89 | 0.88333 | 24275.846 | 25624.504 | 22927.188 | 26973.162 | 28321.82 | 25624.504 | -12137.923 | -13486.581 | -10789.265 | 228.986 | 229.59 | 231.101 | 50.017
2025-10-21 20:45 | 75524.852 | 83616.805 | -37762.426 | 0.89 | 0.90323 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 229.266 | 229.482 | 231.165 | 50.008
2025-10-21 20:46 | 70130.219 | 79570.828 | -35065.109 | 0.89 | 0.88136 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 26973.162 | 24275.846 | -13486.581 | -12137.923 | -9440.606 | 228.597 | 228.209 | 230.259 | 49.999
2025-10-21 20:47 | 72827.539 | 83616.805 | -39111.086 | 0.88 | 0.87097 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -14835.239 | -13486.581 | -10789.265 | 228.727 | 228.597 | 230.302 | 49.97
2025-10-21 20:48 | 72827.539 | 80919.484 | -36413.77 | 0.89 | 0.9 | 25624.504 | 24275.846 | 22927.188 | 28321.82 | 26973.162 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 228.166 | 228.23 | 229.698 | 49.977
2025-10-21 20:49 | 75524.852 | 84965.461 | -37762.426 | 0.89 | 0.88889 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 28321.82 | 26973.162 | -14835.239 | -13486.581 | -10789.265 | 228.533 | 228.533 | 230.41 | 49.996
2025-10-21 20:50 | 68781.563 | 78222.172 | -35065.109 | 0.89 | 0.87931 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 24275.846 | -13486.581 | -12137.923 | -9440.606 | 228.662 | 228.856 | 230.561 | 49.999
2025-10-21 20:51 | 67432.906 | 76873.508 | -36413.77 | 0.88 | 0.87719 | 22927.188 | 22927.188 | 21578.529 | 26973.162 | 25624.504 | 24275.846 | -13486.581 | -13486.581 | -10789.265 | 229.029 | 229.525 | 230.971 | 49.997
2025-10-21 20:52 | 70130.219 | 80919.484 | -37762.426 | 0.88 | 0.86667 | 24275.846 | 24275.846 | 22927.188 | 28321.82 | 26973.162 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 228.317 | 229.072 | 230.388 | 49.994
2025-10-21 20:53 | 72827.539 | 83616.805 | -39111.086 | 0.88 | 0.87097 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 229.137 | 229.655 | 231.101 | 50.014
2025-10-21 20:54 | 74176.195 | 84965.461 | -40459.742 | 0.88 | 0.87302 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 28321.82 | 26973.162 | -14835.239 | -13486.581 | -12137.923 | 229.051 | 229.439 | 231.295 | 49.999
2025-10-21 20:55 | 72827.539 | 83616.805 | -40459.742 | 0.87 | 0.87097 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -14835.239 | -13486.581 | -12137.923 | 229.18 | 229.935 | 231.64 | 50.017
2025-10-21 20:56 | 76873.508 | 87662.773 | -41808.402 | 0.88 | 0.87692 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 29670.479 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 229.288 | 230.216 | 231.877 | 50.021
2025-10-21 20:57 | 74176.195 | 84965.461 | -39111.086 | 0.88 | 0.87302 | 24275.846 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 229.266 | 230.022 | 231.921 | 50.024
2025-10-21 20:58 | 78222.172 | 89011.43 | -40459.742 | 0.88 | 0.87879 | 25624.504 | 26973.162 | 25624.504 | 29670.479 | 31019.137 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 229.633 | 230.302 | 232.158 | 50.026
2025-10-21 20:59 | 74176.195 | 84965.461 | -39111.086 | 0.88 | 0.87302 | 24275.846 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -14835.239 | -13486.581 | -10789.265 | 230.043 | 230.561 | 232.417 | 50.032
2025-10-21 21:00 | 72827.539 | 83616.805 | -39111.086 | 0.88 | 0.87097 | 24275.846 | 26973.162 | 22927.188 | 26973.162 | 31019.137 | 25624.504 | -13486.581 | -14835.239 | -10789.265 | 229.655 | 230.086 | 232.093 | 50.019
2025-10-21 21:01 | 76873.508 | 86314.117 | -40459.742 | 0.88 | 0.89062 | 24275.846 | 28321.82 | 22927.188 | 28321.82 | 32367.793 | 25624.504 | -14835.239 | -16183.896 | -10789.265 | 229.051 | 228.705 | 230.971 | 49.986
2025-10-21 21:02 | 79570.828 | 89011.43 | -39111.086 | 0.89 | 0.89394 | 25624.504 | 28321.82 | 24275.846 | 29670.479 | 32367.793 | 26973.162 | -13486.581 | -14835.239 | -10789.265 | 227.303 | 227.13 | 229.461 | 49.948
2025-10-21 21:03 | 78222.172 | 87662.773 | -39111.086 | 0.89 | 0.89231 | 25624.504 | 26973.162 | 25624.504 | 29670.479 | 31019.137 | 26973.162 | -13486.581 | -14835.239 | -10789.265 | 227.54 | 227.389 | 230.151 | 49.956
2025-10-21 21:04 | 70130.219 | 79570.828 | -36413.77 | 0.89 | 0.88136 | 22927.188 | 25624.504 | 21578.529 | 25624.504 | 28321.82 | 24275.846 | -12137.923 | -13486.581 | -9440.606 | 227.324 | 227.583 | 229.914 | 49.954
2025-10-21 21:05 | 71478.875 | 79570.828 | -35065.109 | 0.89 | 0.89831 | 22927.188 | 25624.504 | 22927.188 | 26973.162 | 28321.82 | 24275.846 | -12137.923 | -13486.581 | -9440.606 | 227.259 | 227.367 | 229.871 | 49.958
2025-10-21 21:06 | 70130.219 | 78222.172 | -35065.109 | 0.89 | 0.89655 | 22927.188 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 24275.846 | -12137.923 | -13486.581 | -9440.606 | 227.518 | 227.842 | 230.108 | 49.963
2025-10-21 21:07 | 72827.539 | 82268.141 | -37762.426 | 0.89 | 0.88525 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 226.806 | 227.41 | 229.266 | 49.974
2025-10-21 21:08 | 72827.539 | 80919.484 | -36413.77 | 0.89 | 0.9 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 227.583 | 227.928 | 229.784 | 49.99
2025-10-21 21:09 | 74176.195 | 82268.141 | -35065.109 | 0.9 | 0.90164 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 25624.504 | -13486.581 | -12137.923 | -9440.606 | 227.108 | 227.216 | 228.943 | 50.007
2025-10-21 21:10 | 75524.852 | 84965.461 | -39111.086 | 0.89 | 0.88889 | 25624.504 | 25624.504 | 24275.846 | 29670.479 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 226.59 | 226.763 | 228.662 | 50.028
2025-10-21 21:11 | 74176.195 | 82268.141 | -35065.109 | 0.9 | 0.90164 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 25624.504 | -13486.581 | -12137.923 | -9440.606 | 226.547 | 226.655 | 228.641 | 50.034
2025-10-21 21:12 | 70130.219 | 79570.828 | -36413.77 | 0.89 | 0.88136 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 226.742 | 227.583 | 228.964 | 50.022
2025-10-21 21:13 | 76873.508 | 86314.117 | -37762.426 | 0.89 | 0.89062 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 29670.479 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 226.936 | 227.605 | 229.288 | 50.016
2025-10-21 21:14 | 78222.172 | 87662.773 | -39111.086 | 0.9 | 0.89231 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -13486.581 | -13486.581 | -10789.265 | 226.849 | 226.936 | 228.792 | 50.02
2025-10-21 21:15 | 79570.828 | 89011.43 | -39111.086 | 0.9 | 0.89394 | 26973.162 | 26973.162 | 25624.504 | 29670.479 | 31019.137 | 28321.82 | -13486.581 | -13486.581 | -10789.265 | 227.518 | 228.058 | 229.763 | 50.015
2025-10-21 21:16 | 79570.828 | 89011.43 | -39111.086 | 0.9 | 0.89394 | 26973.162 | 28321.82 | 25624.504 | 29670.479 | 31019.137 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 226.396 | 226.871 | 228.533 | 50.007
2025-10-21 21:17 | 75524.852 | 86314.117 | -39111.086 | 0.88 | 0.875 | 25624.504 | 26973.162 | 24275.846 | 28321.82 | 31019.137 | 26973.162 | -13486.581 | -14835.239 | -12137.923 | 226.936 | 227.518 | 229.396 | 49.979
2025-10-21 21:18 | 76873.508 | 86314.117 | -39111.086 | 0.89 | 0.89062 | 25624.504 | 26973.162 | 24275.846 | 29670.479 | 29670.479 | 26973.162 | -14835.239 | -13486.581 | -10789.265 | 227.54 | 227.195 | 229.763 | 49.984
2025-10-21 21:19 | 79570.828 | 89011.43 | -39111.086 | 0.89 | 0.89394 | 25624.504 | 26973.162 | 25624.504 | 29670.479 | 31019.137 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 227.108 | 227.022 | 229.612 | 49.975
2025-10-21 21:20 | 75524.852 | 84965.461 | -39111.086 | 0.88 | 0.88889 | 24275.846 | 26973.162 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 227.972 | 228.101 | 230.842 | 49.973
2025-10-21 21:21 | 76873.508 | 86314.117 | -39111.086 | 0.89 | 0.89062 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 29670.479 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 227.367 | 227.605 | 229.978 | 49.978
2025-10-21 21:22 | 78222.172 | 87662.773 | -39111.086 | 0.89 | 0.89231 | 26973.162 | 25624.504 | 25624.504 | 29670.479 | 29670.479 | 28321.82 | -14835.239 | -13486.581 | -12137.923 | 227.173 | 227.281 | 229.439 | 49.986
2025-10-21 21:23 | 75524.852 | 86314.117 | -39111.086 | 0.88 | 0.875 | 25624.504 | 24275.846 | 25624.504 | 29670.479 | 28321.82 | 26973.162 | -14835.239 | -13486.581 | -10789.265 | 226.742 | 226.612 | 228.856 | 49.994
2025-10-21 21:24 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 29670.479 | 26973.162 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -17532.555 | -16183.896 | -12137.923 | 227.475 | 227.799 | 229.655 | 50.01
2025-10-21 21:25 | 87662.773 | 99800.695 | -47203.031 | 0.88 | 0.87838 | 31019.137 | 28321.82 | 28321.82 | 35065.109 | 32367.793 | 31019.137 | -17532.555 | -16183.896 | -13486.581 | 227.82 | 228.619 | 230.216 | 50.012
2025-10-21 21:26 | 84965.461 | 98452.039 | -47203.031 | 0.87 | 0.86301 | 29670.479 | 28321.82 | 28321.82 | 33716.453 | 32367.793 | 31019.137 | -17532.555 | -16183.896 | -13486.581 | 227.044 | 228.446 | 229.935 | 50.018
2025-10-21 21:27 | 84965.461 | 97103.383 | -47203.031 | 0.87 | 0.875 | 29670.479 | 28321.82 | 26973.162 | 33716.453 | 32367.793 | 31019.137 | -16183.896 | -16183.896 | -13486.581 | 227.173 | 228.662 | 229.957 | 50.015
2025-10-21 21:28 | 79570.828 | 91708.75 | -45854.375 | 0.86 | 0.86765 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 227.756 | 229.245 | 230.022 | 50.022
2025-10-21 21:29 | 78222.172 | 90360.094 | -44505.715 | 0.86 | 0.86567 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 227.972 | 228.792 | 230.173 | 50.01
2025-10-21 21:30 | 82268.141 | 95754.727 | -47203.031 | 0.86 | 0.85915 | 28321.82 | 28321.82 | 26973.162 | 33716.453 | 33716.453 | 29670.479 | -17532.555 | -17532.555 | -12137.923 | 228.662 | 229.202 | 230.906 | 49.999
2025-10-21 21:31 | 83616.805 | 94406.063 | -41808.402 | 0.89 | 0.88571 | 26973.162 | 29670.479 | 25624.504 | 31019.137 | 33716.453 | 28321.82 | -14835.239 | -16183.896 | -12137.923 | 228.166 | 228.943 | 230.345 | 49.992
2025-10-21 21:32 | 86314.117 | 98452.039 | -44505.715 | 0.88 | 0.87671 | 28321.82 | 32367.793 | 26973.162 | 31019.137 | 36413.77 | 29670.479 | -14835.239 | -17532.555 | -13486.581 | 228.338 | 229.137 | 231.165 | 49.976
2025-10-21 21:33 | 84965.461 | 95754.727 | -43157.059 | 0.89 | 0.88732 | 26973.162 | 31019.137 | 26973.162 | 31019.137 | 35065.109 | 29670.479 | -14835.239 | -16183.896 | -12137.923 | 227.389 | 227.734 | 229.978 | 49.975
2025-10-21 21:34 | 82268.141 | 93057.406 | -43157.059 | 0.88 | 0.88406 | 25624.504 | 29670.479 | 25624.504 | 29670.479 | 35065.109 | 28321.82 | -14835.239 | -16183.896 | -12137.923 | 228.533 | 228.856 | 231.057 | 49.974
2025-10-21 21:35 | 79570.828 | 90360.094 | -41808.402 | 0.88 | 0.8806 | 25624.504 | 29670.479 | 24275.846 | 29670.479 | 33716.453 | 26973.162 | -14835.239 | -16183.896 | -12137.923 | 229.353 | 229.612 | 231.77 | 49.972
2025-10-21 21:36 | 78222.172 | 87662.773 | -40459.742 | 0.89 | 0.89231 | 24275.846 | 28321.82 | 24275.846 | 28321.82 | 31019.137 | 28321.82 | -13486.581 | -13486.581 | -12137.923 | 230.022 | 230.539 | 232.352 | 49.973
2025-10-21 21:37 | 78222.172 | 87662.773 | -39111.086 | 0.89 | 0.89231 | 25624.504 | 26973.162 | 25624.504 | 29670.479 | 31019.137 | 28321.82 | -13486.581 | -13486.581 | -12137.923 | 230.237 | 230.691 | 232.287 | 49.975
2025-10-21 21:38 | 74176.195 | 83616.805 | -37762.426 | 0.89 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 229.892 | 230.453 | 231.834 | 49.993
2025-10-21 21:39 | 80919.484 | 90360.094 | -41808.402 | 0.88 | 0.89552 | 26973.162 | 26973.162 | 25624.504 | 31019.137 | 31019.137 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 229.547 | 230.367 | 231.489 | 50.021
2025-10-21 21:40 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 28321.82 | 26973.162 | 25624.504 | 33716.453 | 32367.793 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 228.576 | 229.698 | 230.388 | 50.024
2025-10-21 21:41 | 84965.461 | 97103.383 | -45854.375 | 0.88 | 0.875 | 29670.479 | 28321.82 | 26973.162 | 33716.453 | 32367.793 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 229.158 | 230.194 | 231.014 | 50.021
2025-10-21 21:42 | 87662.773 | 99800.695 | -47203.031 | 0.88 | 0.87838 | 29670.479 | 28321.82 | 28321.82 | 35065.109 | 33716.453 | 31019.137 | -17532.555 | -17532.555 | -13486.581 | 228.792 | 230.022 | 231.683 | 50.024
2025-10-21 21:43 | 84965.461 | 95754.727 | -44505.715 | 0.88 | 0.88732 | 29670.479 | 26973.162 | 26973.162 | 33716.453 | 32367.793 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 228.533 | 229.698 | 231.338 | 50.013
2025-10-21 21:44 | 84965.461 | 97103.383 | -45854.375 | 0.88 | 0.875 | 29670.479 | 26973.162 | 28321.82 | 33716.453 | 32367.793 | 31019.137 | -16183.896 | -16183.896 | -12137.923 | 228.986 | 229.763 | 231.511 | 50.018
2025-10-21 21:45 | 82268.141 | 93057.406 | -43157.059 | 0.88 | 0.88406 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 31019.137 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 229.223 | 229.957 | 231.77 | 50.02
2025-10-21 21:46 | 75524.852 | 86314.117 | -41808.402 | 0.87 | 0.875 | 26973.162 | 22927.188 | 25624.504 | 31019.137 | 28321.82 | 26973.162 | -16183.896 | -14835.239 | -10789.265 | 229.309 | 229.137 | 231.77 | 50.006
2025-10-21 21:47 | 76873.508 | 87662.773 | -41808.402 | 0.88 | 0.87692 | 26973.162 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -10789.265 | 229.288 | 228.964 | 231.748 | 49.997
2025-10-21 21:48 | 80919.484 | 91708.75 | -43157.059 | 0.88 | 0.88235 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 230.151 | 230.453 | 232.46 | 50.001
2025-10-21 21:49 | 80919.484 | 91708.75 | -43157.059 | 0.88 | 0.88235 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 230.41 | 230.691 | 232.568 | 49.993
2025-10-21 21:50 | 75524.852 | 86314.117 | -40459.742 | 0.87 | 0.875 | 26973.162 | 24275.846 | 24275.846 | 31019.137 | 28321.82 | 26973.162 | -16183.896 | -14835.239 | -10789.265 | 230.583 | 230.432 | 232.525 | 50.004
2025-10-21 21:51 | 76873.508 | 89011.43 | -43157.059 | 0.87 | 0.86364 | 26973.162 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 230.691 | 230.842 | 232.978 | 50.003
2025-10-21 21:52 | 75524.852 | 83616.805 | -37762.426 | 0.89 | 0.90323 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 231.424 | 231.489 | 233.28 | 50.016
2025-10-21 21:53 | 78222.172 | 89011.43 | -41808.402 | 0.88 | 0.87879 | 25624.504 | 26973.162 | 25624.504 | 29670.479 | 31019.137 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 230.604 | 230.798 | 232.827 | 50.022
2025-10-21 21:54 | 75524.852 | 84965.461 | -37762.426 | 0.89 | 0.88889 | 24275.846 | 26973.162 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 227.993 | 228.619 | 230.324 | 50.031
2025-10-21 21:55 | 75524.852 | 84965.461 | -39111.086 | 0.89 | 0.88889 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 226.957 | 227.281 | 228.878 | 50.041
2025-10-21 21:56 | 70130.219 | 78222.172 | -35065.109 | 0.89 | 0.89655 | 22927.188 | 25624.504 | 21578.529 | 25624.504 | 28321.82 | 24275.846 | -12137.923 | -13486.581 | -9440.606 | 228.058 | 228.015 | 229.849 | 50.045
2025-10-21 21:57 | 74176.195 | 83616.805 | -37762.426 | 0.89 | 0.8871 | 24275.846 | 26973.162 | 22927.188 | 26973.162 | 29670.479 | 25624.504 | -13486.581 | -14835.239 | -9440.606 | 226.763 | 226.332 | 228.77 | 50.041
2025-10-21 21:58 | 71478.875 | 79570.828 | -36413.77 | 0.89 | 0.89831 | 22927.188 | 25624.504 | 22927.188 | 26973.162 | 29670.479 | 24275.846 | -13486.581 | -13486.581 | -9440.606 | 226.785 | 226.051 | 228.921 | 50.031
2025-10-21 21:59 | 70130.219 | 79570.828 | -37762.426 | 0.88 | 0.88136 | 22927.188 | 24275.846 | 22927.188 | 26973.162 | 28321.82 | 24275.846 | -13486.581 | -13486.581 | -10789.265 | 226.871 | 226.483 | 229.007 | 50.033
2025-10-21 22:00 | 68781.563 | 79570.828 | -39111.086 | 0.87 | 0.86441 | 22927.188 | 24275.846 | 21578.529 | 26973.162 | 28321.82 | 24275.846 | -13486.581 | -14835.239 | -10789.265 | 226.936 | 227.108 | 229.072 | 50.032
2025-10-21 22:01 | 62038.273 | 68781.563 | -31019.137 | 0.89 | 0.90196 | 18881.213 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 21578.529 | -10789.265 | -10789.265 | -9440.606 | 227.864 | 228.187 | 229.935 | 49.978
2025-10-21 22:02 | 64735.586 | 72827.539 | -33716.453 | 0.89 | 0.88889 | 21578.529 | 21578.529 | 21578.529 | 24275.846 | 24275.846 | 24275.846 | -12137.923 | -10789.265 | -10789.265 | 227.367 | 228.166 | 229.612 | 49.939
2025-10-21 22:03 | 70130.219 | 79570.828 | -37762.426 | 0.88 | 0.88136 | 24275.846 | 22927.188 | 22927.188 | 28321.82 | 25624.504 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 226.612 | 226.655 | 228.468 | 49.93
2025-10-21 22:04 | 68781.563 | 76873.508 | -36413.77 | 0.88 | 0.89474 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 226.806 | 227 | 228.662 | 49.937
2025-10-21 22:05 | 64735.586 | 74176.195 | -36413.77 | 0.87 | 0.87273 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -13486.581 | -12137.923 | -10789.265 | 227.087 | 227.972 | 229.396 | 49.95
2025-10-21 22:06 | 68781.563 | 76873.508 | -36413.77 | 0.88 | 0.89474 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 226.72 | 226.957 | 228.641 | 49.967
2025-10-21 22:07 | 67432.906 | 76873.508 | -36413.77 | 0.88 | 0.87719 | 24275.846 | 20229.871 | 22927.188 | 26973.162 | 24275.846 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 226.224 | 226.439 | 228.252 | 49.966
2025-10-21 22:08 | 70130.219 | 79570.828 | -36413.77 | 0.88 | 0.88136 | 24275.846 | 21578.529 | 24275.846 | 28321.82 | 25624.504 | 25624.504 | -13486.581 | -12137.923 | -9440.606 | 225.296 | 224.907 | 227.173 | 49.978
2025-10-21 22:09 | 68781.563 | 78222.172 | -36413.77 | 0.88 | 0.87931 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 25624.504 | 24275.846 | -13486.581 | -13486.581 | -9440.606 | 226.202 | 226.094 | 228.166 | 49.99
2025-10-21 22:10 | 71478.875 | 82268.141 | -37762.426 | 0.88 | 0.86885 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 226.655 | 226.677 | 228.835 | 49.992
2025-10-21 22:11 | 66084.242 | 75524.852 | -36413.77 | 0.87 | 0.875 | 22927.188 | 21578.529 | 21578.529 | 26973.162 | 25624.504 | 24275.846 | -13486.581 | -13486.581 | -9440.606 | 227.152 | 226.547 | 228.835 | 50.008
2025-10-21 22:12 | 68781.563 | 76873.508 | -36413.77 | 0.88 | 0.89474 | 22927.188 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 24275.846 | -13486.581 | -12137.923 | -9440.606 | 227.216 | 226.914 | 229.202 | 50.011
2025-10-21 22:13 | 71478.875 | 79570.828 | -36413.77 | 0.88 | 0.89831 | 24275.846 | 22927.188 | 22927.188 | 28321.82 | 26973.162 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 226.742 | 226.763 | 228.727 | 50.02
2025-10-21 22:14 | 66084.242 | 75524.852 | -35065.109 | 0.88 | 0.875 | 24275.846 | 20229.871 | 22927.188 | 26973.162 | 22927.188 | 24275.846 | -13486.581 | -12137.923 | -9440.606 | 226.504 | 225.986 | 228.166 | 50.021
2025-10-21 22:15 | 64735.586 | 75524.852 | -36413.77 | 0.87 | 0.85714 | 22927.188 | 20229.871 | 21578.529 | 26973.162 | 24275.846 | 24275.846 | -13486.581 | -12137.923 | -10789.265 | 226.159 | 226.612 | 227.928 | 50.011
2025-10-21 22:16 | 66084.242 | 75524.852 | -36413.77 | 0.88 | 0.875 | 22927.188 | 20229.871 | 22927.188 | 26973.162 | 24275.846 | 24275.846 | -13486.581 | -12137.923 | -10789.265 | 226.979 | 226.957 | 228.446 | 50.007
2025-10-21 22:17 | 63386.93 | 74176.195 | -36413.77 | 0.86 | 0.85455 | 22927.188 | 20229.871 | 21578.529 | 26973.162 | 22927.188 | 24275.846 | -13486.581 | -12137.923 | -10789.265 | 226.979 | 226.612 | 228.554 | 49.991
2025-10-21 22:18 | 67432.906 | 78222.172 | -37762.426 | 0.87 | 0.86207 | 24275.846 | 20229.871 | 22927.188 | 28321.82 | 24275.846 | 25624.504 | -14835.239 | -13486.581 | -10789.265 | 227.173 | 226.763 | 228.662 | 49.992
2025-10-21 22:19 | 62038.273 | 71478.875 | -35065.109 | 0.87 | 0.86792 | 21578.529 | 18881.213 | 20229.871 | 25624.504 | 22927.188 | 22927.188 | -13486.581 | -12137.923 | -10789.265 | 227.238 | 227.216 | 228.619 | 49.984
2025-10-21 22:20 | 66084.242 | 76873.508 | -37762.426 | 0.87 | 0.85965 | 24275.846 | 20229.871 | 22927.188 | 26973.162 | 24275.846 | 24275.846 | -13486.581 | -13486.581 | -10789.265 | 227.626 | 227.152 | 228.921 | 50.005
2025-10-21 22:21 | 66084.242 | 76873.508 | -36413.77 | 0.87 | 0.85965 | 24275.846 | 20229.871 | 22927.188 | 26973.162 | 24275.846 | 24275.846 | -13486.581 | -12137.923 | -10789.265 | 227.41 | 226.634 | 228.835 | 49.992
2025-10-21 22:22 | 66084.242 | 75524.852 | -36413.77 | 0.87 | 0.875 | 22927.188 | 20229.871 | 22927.188 | 26973.162 | 24275.846 | 24275.846 | -13486.581 | -12137.923 | -10789.265 | 226.655 | 226.483 | 228.382 | 50.003
2025-10-21 22:23 | 66084.242 | 75524.852 | -35065.109 | 0.88 | 0.875 | 22927.188 | 20229.871 | 22927.188 | 26973.162 | 24275.846 | 24275.846 | -13486.581 | -12137.923 | -9440.606 | 226.59 | 226.461 | 227.972 | 49.996
2025-10-21 22:24 | 70130.219 | 79570.828 | -36413.77 | 0.88 | 0.88136 | 24275.846 | 21578.529 | 24275.846 | 28321.82 | 25624.504 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 227.303 | 227.044 | 228.792 | 50.012
2025-10-21 22:25 | 67432.906 | 76873.508 | -36413.77 | 0.87 | 0.87719 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 227.605 | 227.885 | 229.223 | 50.004
2025-10-21 22:26 | 71478.875 | 80919.484 | -37762.426 | 0.88 | 0.88333 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 28321.82 | 25624.504 | -13486.581 | -14835.239 | -10789.265 | 227.41 | 227.518 | 229.051 | 50.012
2025-10-21 22:27 | 71478.875 | 80919.484 | -39111.086 | 0.88 | 0.88333 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 28321.82 | 25624.504 | -13486.581 | -14835.239 | -10789.265 | 227.54 | 227.648 | 229.245 | 50.014
2025-10-21 22:28 | 68781.563 | 78222.172 | -36413.77 | 0.88 | 0.87931 | 22927.188 | 22927.188 | 22927.188 | 26973.162 | 26973.162 | 24275.846 | -13486.581 | -13486.581 | -9440.606 | 228.727 | 228.489 | 230.453 | 50.014
2025-10-21 22:29 | 70130.219 | 79570.828 | -37762.426 | 0.88 | 0.88136 | 22927.188 | 24275.846 | 22927.188 | 26973.162 | 28321.82 | 24275.846 | -13486.581 | -14835.239 | -9440.606 | 227.928 | 227.303 | 229.655 | 50
2025-10-21 22:30 | 68781.563 | 78222.172 | -37762.426 | 0.87 | 0.87931 | 22927.188 | 24275.846 | 21578.529 | 26973.162 | 28321.82 | 24275.846 | -13486.581 | -14835.239 | -9440.606 | 227.41 | 226.72 | 229.396 | 49.993
2025-10-21 22:31 | 68781.563 | 78222.172 | -37762.426 | 0.87 | 0.87931 | 22927.188 | 24275.846 | 21578.529 | 26973.162 | 28321.82 | 24275.846 | -13486.581 | -14835.239 | -10789.265 | 227.518 | 227.303 | 229.612 | 49.97
2025-10-21 22:32 | 72827.539 | 83616.805 | -40459.742 | 0.87 | 0.87097 | 24275.846 | 25624.504 | 22927.188 | 28321.82 | 29670.479 | 25624.504 | -13486.581 | -14835.239 | -10789.265 | 228.079 | 227.993 | 230.173 | 49.956
2025-10-21 22:33 | 71478.875 | 83616.805 | -41808.402 | 0.86 | 0.85484 | 24275.846 | 25624.504 | 22927.188 | 28321.82 | 29670.479 | 25624.504 | -14835.239 | -16183.896 | -12137.923 | 228.123 | 228.144 | 230.237 | 49.976
2025-10-21 22:34 | 62038.273 | 72827.539 | -36413.77 | 0.86 | 0.85185 | 21578.529 | 20229.871 | 20229.871 | 25624.504 | 24275.846 | 22927.188 | -13486.581 | -13486.581 | -10789.265 | 227.907 | 228.36 | 229.935 | 49.986
2025-10-21 22:35 | 62038.273 | 72827.539 | -36413.77 | 0.86 | 0.85185 | 21578.529 | 20229.871 | 20229.871 | 25624.504 | 22927.188 | 22927.188 | -13486.581 | -13486.581 | -10789.265 | 228.274 | 228.446 | 229.741 | 49.989
2025-10-21 22:36 | 64735.586 | 74176.195 | -35065.109 | 0.88 | 0.87273 | 21578.529 | 21578.529 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 228.144 | 228.856 | 230.086 | 49.996
2025-10-21 22:37 | 63386.93 | 71478.875 | -32367.793 | 0.89 | 0.88679 | 21578.529 | 21578.529 | 21578.529 | 24275.846 | 24275.846 | 24275.846 | -10789.265 | -10789.265 | -10789.265 | 227.669 | 228.23 | 229.331 | 50.021
2025-10-21 22:38 | 66084.242 | 74176.195 | -33716.453 | 0.89 | 0.89091 | 21578.529 | 21578.529 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -10789.265 | -10789.265 | -10789.265 | 227.54 | 228.209 | 229.137 | 50.038
2025-10-21 22:39 | 64735.586 | 72827.539 | -33716.453 | 0.89 | 0.88889 | 21578.529 | 21578.529 | 21578.529 | 24275.846 | 24275.846 | 24275.846 | -10789.265 | -10789.265 | -10789.265 | 228.23 | 228.77 | 230.022 | 50.024
2025-10-21 22:40 | 67432.906 | 76873.508 | -35065.109 | 0.89 | 0.87719 | 22927.188 | 22927.188 | 22927.188 | 25624.504 | 25624.504 | 25624.504 | -12137.923 | -12137.923 | -12137.923 | 227.605 | 228.382 | 229.612 | 50.016
2025-10-21 22:41 | 66084.242 | 74176.195 | -33716.453 | 0.89 | 0.89091 | 21578.529 | 21578.529 | 22927.188 | 24275.846 | 24275.846 | 25624.504 | -12137.923 | -10789.265 | -10789.265 | 227.518 | 228.468 | 229.547 | 50.017
2025-10-21 22:42 | 71478.875 | 80919.484 | -39111.086 | 0.88 | 0.88333 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 227.626 | 228.338 | 229.568 | 50.027
2025-10-21 22:43 | 71478.875 | 82268.141 | -39111.086 | 0.88 | 0.86885 | 25624.504 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 227.367 | 228.295 | 229.461 | 50.023
2025-10-21 22:44 | 67432.906 | 76873.508 | -37762.426 | 0.87 | 0.87719 | 24275.846 | 21578.529 | 21578.529 | 26973.162 | 25624.504 | 24275.846 | -13486.581 | -13486.581 | -10789.265 | 226.979 | 228.015 | 228.77 | 50.007
2025-10-21 22:45 | 72827.539 | 83616.805 | -39111.086 | 0.88 | 0.87097 | 24275.846 | 24275.846 | 22927.188 | 28321.82 | 28321.82 | 25624.504 | -13486.581 | -14835.239 | -10789.265 | 226.957 | 227.756 | 229.007 | 50.023
2025-10-21 22:46 | 71478.875 | 82268.141 | -40459.742 | 0.87 | 0.86885 | 24275.846 | 24275.846 | 22927.188 | 28321.82 | 28321.82 | 25624.504 | -13486.581 | -14835.239 | -10789.265 | 227.173 | 227.993 | 229.115 | 50.008
2025-10-21 22:47 | 74176.195 | 84965.461 | -40459.742 | 0.87 | 0.87302 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 28321.82 | 26973.162 | -14835.239 | -14835.239 | -12137.923 | 227.777 | 228.187 | 229.806 | 49.992
2025-10-21 22:48 | 68781.563 | 79570.828 | -40459.742 | 0.86 | 0.86441 | 22927.188 | 22927.188 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -14835.239 | -14835.239 | -12137.923 | 227.626 | 228.295 | 229.763 | 50.008
2025-10-21 22:49 | 66084.242 | 76873.508 | -37762.426 | 0.86 | 0.85965 | 22927.188 | 22927.188 | 21578.529 | 25624.504 | 26973.162 | 24275.846 | -13486.581 | -13486.581 | -10789.265 | 227.972 | 229.18 | 229.827 | 50.008
2025-10-21 22:50 | 66084.242 | 74176.195 | -33716.453 | 0.89 | 0.89091 | 21578.529 | 22927.188 | 21578.529 | 24275.846 | 25624.504 | 24275.846 | -10789.265 | -12137.923 | -10789.265 | 227.583 | 228.489 | 229.245 | 50.021
2025-10-21 22:51 | 64735.586 | 72827.539 | -32367.793 | 0.89 | 0.88889 | 21578.529 | 21578.529 | 21578.529 | 24275.846 | 24275.846 | 24275.846 | -10789.265 | -10789.265 | -10789.265 | 228.748 | 229.482 | 230.518 | 50.015
2025-10-21 22:52 | 64735.586 | 72827.539 | -32367.793 | 0.89 | 0.88889 | 21578.529 | 21578.529 | 21578.529 | 24275.846 | 24275.846 | 24275.846 | -10789.265 | -10789.265 | -10789.265 | 227.842 | 228.878 | 229.633 | 50.024
2025-10-21 22:53 | 63386.93 | 71478.875 | -32367.793 | 0.89 | 0.88679 | 21578.529 | 21578.529 | 21578.529 | 24275.846 | 24275.846 | 24275.846 | -10789.265 | -10789.265 | -10789.265 | 228.015 | 229.374 | 229.741 | 50.029
2025-10-21 22:54 | 66084.242 | 74176.195 | -33716.453 | 0.89 | 0.89091 | 21578.529 | 21578.529 | 21578.529 | 24275.846 | 25624.504 | 24275.846 | -10789.265 | -12137.923 | -12137.923 | 228.079 | 229.158 | 229.892 | 50.04
2025-10-21 22:55 | 66084.242 | 74176.195 | -35065.109 | 0.89 | 0.89091 | 21578.529 | 21578.529 | 21578.529 | 24275.846 | 24275.846 | 24275.846 | -12137.923 | -10789.265 | -10789.265 | 228.23 | 229.094 | 230.043 | 50.025
2025-10-21 22:56 | 66084.242 | 74176.195 | -32367.793 | 0.89 | 0.89091 | 21578.529 | 21578.529 | 21578.529 | 24275.846 | 24275.846 | 24275.846 | -10789.265 | -10789.265 | -10789.265 | 228.425 | 229.245 | 230.108 | 50.033
2025-10-21 22:57 | 66084.242 | 74176.195 | -33716.453 | 0.89 | 0.89091 | 21578.529 | 22927.188 | 21578.529 | 24275.846 | 25624.504 | 24275.846 | -10789.265 | -10789.265 | -10789.265 | 228.468 | 229.978 | 230.216 | 50.033
2025-10-21 22:58 | 66084.242 | 74176.195 | -33716.453 | 0.89 | 0.89091 | 21578.529 | 22927.188 | 21578.529 | 24275.846 | 25624.504 | 24275.846 | -10789.265 | -12137.923 | -12137.923 | 228.36 | 229.763 | 230.022 | 50.024
2025-10-21 22:59 | 64735.586 | 72827.539 | -33716.453 | 0.89 | 0.88889 | 21578.529 | 21578.529 | 21578.529 | 24275.846 | 24275.846 | 24275.846 | -10789.265 | -10789.265 | -10789.265 | 228.101 | 229.353 | 230.259 | 50.023
2025-10-21 23:00 | 63386.93 | 71478.875 | -32367.793 | 0.89 | 0.88679 | 21578.529 | 21578.529 | 21578.529 | 24275.846 | 24275.846 | 24275.846 | -10789.265 | -10789.265 | -10789.265 | 228.511 | 229.568 | 230.583 | 50.024
2025-10-21 23:01 | 66084.242 | 74176.195 | -35065.109 | 0.89 | 0.89091 | 21578.529 | 22927.188 | 21578.529 | 24275.846 | 25624.504 | 24275.846 | -10789.265 | -12137.923 | -12137.923 | 228.338 | 229.525 | 230.281 | 49.986
2025-10-21 23:02 | 67432.906 | 75524.852 | -35065.109 | 0.89 | 0.89286 | 21578.529 | 22927.188 | 21578.529 | 24275.846 | 25624.504 | 25624.504 | -12137.923 | -10789.265 | -12137.923 | 228.295 | 229.331 | 230.259 | 49.956
2025-10-21 23:03 | 66084.242 | 74176.195 | -33716.453 | 0.89 | 0.89091 | 21578.529 | 22927.188 | 21578.529 | 24275.846 | 25624.504 | 24275.846 | -10789.265 | -12137.923 | -10789.265 | 228.403 | 229.158 | 230.453 | 49.965
2025-10-21 23:04 | 66084.242 | 74176.195 | -33716.453 | 0.89 | 0.89091 | 21578.529 | 24275.846 | 21578.529 | 24275.846 | 26973.162 | 24275.846 | -10789.265 | -12137.923 | -10789.265 | 227.993 | 228.554 | 230.022 | 49.968
2025-10-21 23:05 | 66084.242 | 74176.195 | -33716.453 | 0.89 | 0.89091 | 21578.529 | 24275.846 | 21578.529 | 24275.846 | 26973.162 | 24275.846 | -10789.265 | -12137.923 | -10789.265 | 228.317 | 228.792 | 230.237 | 49.974
2025-10-21 23:06 | 67432.906 | 75524.852 | -35065.109 | 0.89 | 0.89286 | 21578.529 | 24275.846 | 21578.529 | 24275.846 | 26973.162 | 24275.846 | -10789.265 | -12137.923 | -10789.265 | 227.885 | 228.489 | 229.957 | 49.965
2025-10-21 23:07 | 67432.906 | 75524.852 | -35065.109 | 0.89 | 0.89286 | 21578.529 | 24275.846 | 21578.529 | 24275.846 | 26973.162 | 24275.846 | -10789.265 | -12137.923 | -10789.265 | 227.972 | 228.317 | 230.108 | 49.977
2025-10-21 23:08 | 68781.563 | 76873.508 | -35065.109 | 0.89 | 0.89474 | 21578.529 | 25624.504 | 21578.529 | 24275.846 | 28321.82 | 24275.846 | -10789.265 | -13486.581 | -10789.265 | 228.295 | 228.425 | 230.216 | 49.973
2025-10-21 23:09 | 70130.219 | 79570.828 | -37762.426 | 0.88 | 0.88136 | 21578.529 | 25624.504 | 21578.529 | 25624.504 | 29670.479 | 24275.846 | -12137.923 | -13486.581 | -12137.923 | 229.115 | 229.223 | 231.165 | 49.977
2025-10-21 23:10 | 67432.906 | 75524.852 | -35065.109 | 0.89 | 0.89286 | 21578.529 | 24275.846 | 21578.529 | 24275.846 | 26973.162 | 24275.846 | -10789.265 | -12137.923 | -10789.265 | 228.252 | 228.835 | 230.345 | 49.995
2025-10-21 23:11 | 67432.906 | 76873.508 | -36413.77 | 0.88 | 0.87719 | 21578.529 | 24275.846 | 21578.529 | 25624.504 | 26973.162 | 24275.846 | -12137.923 | -12137.923 | -12137.923 | 228.705 | 229.331 | 230.669 | 50.011
2025-10-21 23:12 | 66084.242 | 74176.195 | -33716.453 | 0.89 | 0.89091 | 21578.529 | 24275.846 | 21578.529 | 24275.846 | 26973.162 | 24275.846 | -10789.265 | -12137.923 | -10789.265 | 228.36 | 229.115 | 230.863 | 50.02
2025-10-21 23:13 | 67432.906 | 75524.852 | -35065.109 | 0.89 | 0.89286 | 21578.529 | 24275.846 | 21578.529 | 24275.846 | 26973.162 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 227.885 | 228.468 | 230.432 | 50.029
2025-10-21 23:14 | 67432.906 | 75524.852 | -33716.453 | 0.89 | 0.89286 | 21578.529 | 24275.846 | 21578.529 | 24275.846 | 26973.162 | 24275.846 | -10789.265 | -12137.923 | -10789.265 | 227.648 | 227.972 | 230.086 | 50.012
2025-10-21 23:15 | 66084.242 | 74176.195 | -33716.453 | 0.89 | 0.89091 | 21578.529 | 22927.188 | 21578.529 | 24275.846 | 25624.504 | 24275.846 | -10789.265 | -10789.265 | -10789.265 | 228.036 | 228.856 | 230.281 | 49.995
2025-10-21 23:16 | 78222.172 | 90360.094 | -43157.059 | 0.88 | 0.86567 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 29670.479 | 29670.479 | -14835.239 | -14835.239 | -13486.581 | 226.137 | 227.324 | 228.748 | 49.991
2025-10-21 23:17 | 78222.172 | 90360.094 | -45854.375 | 0.86 | 0.86567 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.461 | 227.54 | 228.748 | 49.99
2025-10-21 23:18 | 78222.172 | 91708.75 | -45854.375 | 0.86 | 0.85294 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 226.31 | 227.583 | 228.576 | 49.989
2025-10-21 23:19 | 78222.172 | 91708.75 | -45854.375 | 0.86 | 0.85294 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 28321.82 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 226.655 | 227.691 | 229.223 | 50
2025-10-21 23:20 | 79570.828 | 91708.75 | -45854.375 | 0.87 | 0.86765 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 226.439 | 227.907 | 229.115 | 50.005
2025-10-21 23:21 | 78222.172 | 90360.094 | -44505.715 | 0.86 | 0.86567 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.439 | 227.799 | 228.878 | 50.012
2025-10-21 23:22 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 31019.137 | -17532.555 | -16183.896 | -13486.581 | 226.267 | 227.41 | 228.446 | 50.008
2025-10-21 23:23 | 80919.484 | 91708.75 | -43157.059 | 0.88 | 0.88235 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.735 | 225.965 | 227 | 49.997
2025-10-21 23:24 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 29670.479 | 25624.504 | 28321.82 | 33716.453 | 31019.137 | 31019.137 | -16183.896 | -16183.896 | -13486.581 | 224.799 | 226.18 | 227.281 | 50.002
2025-10-21 23:25 | 80919.484 | 94406.063 | -47203.031 | 0.86 | 0.85714 | 28321.82 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -17532.555 | -16183.896 | -13486.581 | 224.994 | 226.288 | 227.281 | 50.003
2025-10-21 23:26 | 78222.172 | 90360.094 | -43157.059 | 0.87 | 0.86567 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 28321.82 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 224.174 | 225.598 | 226.569 | 50.016
2025-10-21 23:27 | 71478.875 | 83616.805 | -43157.059 | 0.85 | 0.85484 | 25624.504 | 21578.529 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -16183.896 | -14835.239 | -12137.923 | 225.123 | 226.396 | 227.324 | 50.001
2025-10-21 23:28 | 71478.875 | 83616.805 | -43157.059 | 0.85 | 0.85484 | 25624.504 | 21578.529 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -16183.896 | -14835.239 | -12137.923 | 225.792 | 227.173 | 228.209 | 50.012
2025-10-21 23:29 | 70130.219 | 80919.484 | -40459.742 | 0.87 | 0.86667 | 24275.846 | 21578.529 | 22927.188 | 28321.82 | 25624.504 | 25624.504 | -14835.239 | -13486.581 | -12137.923 | 224.907 | 226.569 | 227.195 | 49.999
2025-10-21 23:30 | 70130.219 | 79570.828 | -37762.426 | 0.88 | 0.88136 | 22927.188 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 224.195 | 225.576 | 226.353 | 50.007
2025-10-21 23:31 | 70130.219 | 79570.828 | -36413.77 | 0.88 | 0.88136 | 22927.188 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -12137.923 | -13486.581 | -10789.265 | 224.713 | 225.943 | 227.13 | 49.994
2025-10-21 23:32 | 74176.195 | 84965.461 | -40459.742 | 0.88 | 0.87302 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -14835.239 | -12137.923 | 226.008 | 227.022 | 228.533 | 49.983
2025-10-21 23:33 | 71478.875 | 80919.484 | -37762.426 | 0.88 | 0.88333 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 28321.82 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 225.123 | 226.288 | 227.583 | 50.01
2025-10-21 23:34 | 68781.563 | 79570.828 | -39111.086 | 0.87 | 0.86441 | 22927.188 | 24275.846 | 21578.529 | 26973.162 | 28321.82 | 24275.846 | -13486.581 | -14835.239 | -10789.265 | 226.439 | 227.281 | 228.792 | 50.011
2025-10-21 23:35 | 66084.242 | 75524.852 | -36413.77 | 0.87 | 0.875 | 21578.529 | 22927.188 | 20229.871 | 25624.504 | 26973.162 | 22927.188 | -12137.923 | -13486.581 | -9440.606 | 226.698 | 227.281 | 228.813 | 50.008
2025-10-21 23:36 | 75524.852 | 86314.117 | -40459.742 | 0.88 | 0.875 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -13486.581 | -14835.239 | -12137.923 | 225.943 | 226.763 | 228.144 | 50.013
2025-10-21 23:37 | 72827.539 | 83616.805 | -39111.086 | 0.88 | 0.87097 | 24275.846 | 25624.504 | 24275.846 | 28321.82 | 28321.82 | 25624.504 | -13486.581 | -14835.239 | -10789.265 | 225.857 | 226.547 | 228.209 | 50.015
2025-10-21 23:38 | 72827.539 | 82268.141 | -39111.086 | 0.88 | 0.88525 | 24275.846 | 24275.846 | 22927.188 | 28321.82 | 28321.82 | 25624.504 | -13486.581 | -14835.239 | -10789.265 | 226.31 | 226.936 | 228.813 | 50.023
2025-10-21 23:39 | 72827.539 | 82268.141 | -39111.086 | 0.88 | 0.88525 | 24275.846 | 25624.504 | 22927.188 | 28321.82 | 29670.479 | 25624.504 | -13486.581 | -14835.239 | -10789.265 | 226.871 | 227.518 | 229.202 | 50.022
2025-10-21 23:40 | 75524.852 | 86314.117 | -43157.059 | 0.87 | 0.875 | 25624.504 | 25624.504 | 24275.846 | 29670.479 | 29670.479 | 26973.162 | -14835.239 | -16183.896 | -12137.923 | 226.936 | 227.777 | 229.288 | 50.02
2025-10-21 23:41 | 72827.539 | 83616.805 | -40459.742 | 0.88 | 0.87097 | 25624.504 | 22927.188 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -14835.239 | -13486.581 | -12137.923 | 227.13 | 227.756 | 229.137 | 50.031
2025-10-21 23:42 | 79570.828 | 91708.75 | -44505.715 | 0.87 | 0.86765 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 226.849 | 227.259 | 229.158 | 50.033
2025-10-21 23:43 | 80919.484 | 93057.406 | -45854.375 | 0.87 | 0.86957 | 28321.82 | 24275.846 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 226.979 | 227.583 | 229.568 | 50.024
2025-10-21 23:44 | 76873.508 | 90360.094 | -47203.031 | 0.85 | 0.85075 | 28321.82 | 22927.188 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -17532.555 | -17532.555 | -13486.581 | 226.655 | 227.367 | 228.943 | 50.019
2025-10-21 23:45 | 80919.484 | 93057.406 | -47203.031 | 0.86 | 0.86957 | 28321.82 | 24275.846 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -17532.555 | -17532.555 | -13486.581 | 226.59 | 227.259 | 229.072 | 50.008
2025-10-21 23:46 | 78222.172 | 91708.75 | -45854.375 | 0.86 | 0.85294 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 29670.479 | -17532.555 | -16183.896 | -13486.581 | 227.281 | 228.058 | 229.935 | 50.019
2025-10-21 23:47 | 83616.805 | 97103.383 | -48551.691 | 0.86 | 0.86111 | 29670.479 | 25624.504 | 28321.82 | 35065.109 | 31019.137 | 31019.137 | -17532.555 | -17532.555 | -13486.581 | 226.936 | 227.864 | 229.655 | 50.019
2025-10-21 23:48 | 83616.805 | 98452.039 | -49900.348 | 0.86 | 0.84932 | 29670.479 | 25624.504 | 28321.82 | 35065.109 | 32367.793 | 31019.137 | -17532.555 | -17532.555 | -14835.239 | 227.152 | 228.036 | 229.655 | 50.006
2025-10-21 23:49 | 79570.828 | 93057.406 | -45854.375 | 0.86 | 0.85507 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 226.936 | 227.691 | 229.525 | 50.015
2025-10-21 23:50 | 83616.805 | 95754.727 | -47203.031 | 0.87 | 0.87324 | 29670.479 | 26973.162 | 26973.162 | 33716.453 | 32367.793 | 31019.137 | -16183.896 | -17532.555 | -13486.581 | 226.677 | 227.691 | 229.482 | 50.034
2025-10-21 23:51 | 78222.172 | 91708.75 | -45854.375 | 0.86 | 0.85294 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 227.583 | 228.295 | 229.741 | 50.022
2025-10-21 23:52 | 75524.852 | 87662.773 | -44505.715 | 0.85 | 0.86154 | 26973.162 | 24275.846 | 24275.846 | 31019.137 | 29670.479 | 26973.162 | -16183.896 | -16183.896 | -12137.923 | 227.475 | 227.95 | 229.374 | 50.033
2025-10-21 23:53 | 71478.875 | 83616.805 | -41808.402 | 0.86 | 0.85484 | 25624.504 | 22927.188 | 22927.188 | 29670.479 | 28321.82 | 25624.504 | -14835.239 | -16183.896 | -10789.265 | 227.605 | 228.166 | 229.784 | 50.031
2025-10-21 23:54 | 74176.195 | 86314.117 | -44505.715 | 0.85 | 0.85938 | 25624.504 | 24275.846 | 24275.846 | 31019.137 | 28321.82 | 26973.162 | -16183.896 | -16183.896 | -12137.923 | 227.54 | 228.295 | 229.957 | 50.032
2025-10-21 23:55 | 71478.875 | 84965.461 | -45854.375 | 0.84 | 0.84127 | 25624.504 | 22927.188 | 22927.188 | 29670.479 | 28321.82 | 26973.162 | -16183.896 | -16183.896 | -12137.923 | 228.23 | 229.547 | 231.014 | 50.043
2025-10-21 23:56 | 67432.906 | 78222.172 | -39111.086 | 0.87 | 0.86207 | 22927.188 | 21578.529 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 228.166 | 229.245 | 230.194 | 50.045
2025-10-21 23:57 | 76873.508 | 87662.773 | -41808.402 | 0.88 | 0.87692 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 29670.479 | -14835.239 | -14835.239 | -12137.923 | 227.842 | 229.18 | 230.065 | 50.042
2025-10-21 23:58 | 75524.852 | 84965.461 | -37762.426 | 0.89 | 0.88889 | 25624.504 | 24275.846 | 25624.504 | 29670.479 | 26973.162 | 28321.82 | -13486.581 | -13486.581 | -10789.265 | 227.734 | 228.727 | 229.698 | 50.029
2025-10-21 23:59 | 82268.141 | 93057.406 | -43157.059 | 0.88 | 0.88406 | 29670.479 | 25624.504 | 28321.82 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 227.756 | 228.835 | 229.892 | 50.043
2025-10-22 | 80919.484 | 91708.75 | -41808.402 | 0.89 | 0.88235 | 29670.479 | 24275.846 | 26973.162 | 32367.793 | 28321.82 | 29670.479 | -16183.896 | -14835.239 | -10789.265 | 227.108 | 228.123 | 229.309 | 50.039
2025-10-22 00:01 | 75524.852 | 87662.773 | -41808.402 | 0.87 | 0.86154 | 26973.162 | 22927.188 | 25624.504 | 31019.137 | 26973.162 | 28321.82 | -16183.896 | -14835.239 | -10789.265 | 227.648 | 228.489 | 229.978 | 49.979
2025-10-22 00:02 | 80919.484 | 93057.406 | -45854.375 | 0.87 | 0.86957 | 28321.82 | 24275.846 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 227.216 | 228.166 | 229.612 | 49.925
2025-10-22 00:03 | 78222.172 | 90360.094 | -43157.059 | 0.87 | 0.86567 | 26973.162 | 25624.504 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -10789.265 | 227 | 227.303 | 229.417 | 49.937
2025-10-22 00:04 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 28321.82 | 26973.162 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 226.806 | 227.324 | 229.309 | 49.954
2025-10-22 00:05 | 83616.805 | 94406.063 | -44505.715 | 0.88 | 0.88571 | 28321.82 | 26973.162 | 26973.162 | 33716.453 | 32367.793 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 226.849 | 227.842 | 229.547 | 49.956
2025-10-22 00:06 | 82268.141 | 94406.063 | -47203.031 | 0.87 | 0.87143 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 32367.793 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 227.065 | 228.058 | 229.763 | 49.97
2025-10-22 00:07 | 80919.484 | 93057.406 | -45854.375 | 0.87 | 0.86957 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 31019.137 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 226.612 | 227.605 | 229.288 | 49.975
2025-10-22 00:08 | 80919.484 | 93057.406 | -45854.375 | 0.87 | 0.86957 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.353 | 227.259 | 229.158 | 49.986
2025-10-22 00:09 | 76873.508 | 89011.43 | -44505.715 | 0.86 | 0.86364 | 26973.162 | 22927.188 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.029 | 227.108 | 228.748 | 49.986
2025-10-22 00:10 | 79570.828 | 91708.75 | -44505.715 | 0.87 | 0.86765 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.986 | 227.087 | 228.835 | 49.991
2025-10-22 00:11 | 75524.852 | 86314.117 | -43157.059 | 0.86 | 0.875 | 26973.162 | 22927.188 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 225.77 | 226.828 | 228.489 | 49.979
2025-10-22 00:12 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 226.396 | 227.497 | 229.029 | 49.978
2025-10-22 00:13 | 80919.484 | 91708.75 | -43157.059 | 0.88 | 0.88235 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.18 | 227.087 | 229.094 | 49.992
2025-10-22 00:14 | 79570.828 | 91708.75 | -44505.715 | 0.87 | 0.86765 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 225.706 | 226.569 | 228.554 | 49.987
2025-10-22 00:15 | 80919.484 | 91708.75 | -44505.715 | 0.87 | 0.88235 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.288 | 227.108 | 229.029 | 49.987
2025-10-22 00:16 | 78222.172 | 90360.094 | -43157.059 | 0.87 | 0.86567 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -10789.265 | 226.742 | 227.41 | 229.461 | 49.983
2025-10-22 00:17 | 86314.117 | 98452.039 | -47203.031 | 0.87 | 0.87671 | 29670.479 | 28321.82 | 28321.82 | 35065.109 | 32367.793 | 31019.137 | -17532.555 | -17532.555 | -13486.581 | 226.245 | 226.979 | 229.051 | 49.984
2025-10-22 00:18 | 78222.172 | 90360.094 | -44505.715 | 0.86 | 0.86567 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.375 | 227.13 | 228.835 | 49.987
2025-10-22 00:19 | 74176.195 | 84965.461 | -41808.402 | 0.87 | 0.87302 | 26973.162 | 22927.188 | 24275.846 | 31019.137 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 226.698 | 227.691 | 229.051 | 49.981
2025-10-22 00:20 | 71478.875 | 83616.805 | -41808.402 | 0.86 | 0.85484 | 25624.504 | 21578.529 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -12137.923 | 226.634 | 227.562 | 228.943 | 49.979
2025-10-22 00:21 | 71478.875 | 82268.141 | -40459.742 | 0.86 | 0.86885 | 25624.504 | 21578.529 | 22927.188 | 29670.479 | 25624.504 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 226.677 | 227.691 | 228.899 | 49.984
2025-10-22 00:22 | 76873.508 | 87662.773 | -41808.402 | 0.87 | 0.87692 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 226.353 | 227.583 | 228.468 | 49.991
2025-10-22 00:23 | 79570.828 | 91708.75 | -43157.059 | 0.88 | 0.86765 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 226.547 | 227.885 | 228.748 | 50.005
2025-10-22 00:24 | 87662.773 | 99800.695 | -47203.031 | 0.87 | 0.87838 | 31019.137 | 26973.162 | 28321.82 | 35065.109 | 32367.793 | 32367.793 | -17532.555 | -17532.555 | -13486.581 | 226.957 | 228.166 | 229.158 | 50.003
2025-10-22 00:25 | 80919.484 | 94406.063 | -47203.031 | 0.86 | 0.85714 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 226.936 | 227.972 | 229.094 | 50.005
2025-10-22 00:26 | 72827.539 | 83616.805 | -43157.059 | 0.86 | 0.87097 | 25624.504 | 21578.529 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -16183.896 | -14835.239 | -12137.923 | 227.281 | 228.317 | 229.633 | 49.995
2025-10-22 00:27 | 67432.906 | 79570.828 | -41808.402 | 0.85 | 0.84746 | 24275.846 | 20229.871 | 22927.188 | 28321.82 | 25624.504 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 226.936 | 228.187 | 229.223 | 50.004
2025-10-22 00:28 | 67432.906 | 80919.484 | -43157.059 | 0.84 | 0.83333 | 24275.846 | 21578.529 | 21578.529 | 28321.82 | 26973.162 | 24275.846 | -16183.896 | -16183.896 | -12137.923 | 226.742 | 227.972 | 229.029 | 49.987
2025-10-22 00:29 | 78222.172 | 90360.094 | -43157.059 | 0.87 | 0.86567 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 31019.137 | 28321.82 | -14835.239 | -16183.896 | -12137.923 | 226.957 | 228.209 | 229.525 | 50.009
2025-10-22 00:30 | 86314.117 | 98452.039 | -47203.031 | 0.87 | 0.87671 | 29670.479 | 28321.82 | 26973.162 | 33716.453 | 33716.453 | 31019.137 | -16183.896 | -17532.555 | -13486.581 | 226.763 | 227.928 | 229.525 | 49.998
2025-10-22 00:31 | 86314.117 | 98452.039 | -47203.031 | 0.87 | 0.87671 | 29670.479 | 29670.479 | 26973.162 | 33716.453 | 35065.109 | 29670.479 | -16183.896 | -18881.213 | -12137.923 | 227.82 | 228.252 | 230.712 | 50.003
2025-10-22 00:32 | 91708.75 | 103846.672 | -49900.348 | 0.88 | 0.88312 | 31019.137 | 31019.137 | 29670.479 | 35065.109 | 36413.77 | 32367.793 | -17532.555 | -18881.213 | -13486.581 | 228.015 | 228.403 | 231.144 | 50
2025-10-22 00:33 | 90360.094 | 103846.672 | -51249.008 | 0.87 | 0.87013 | 31019.137 | 31019.137 | 28321.82 | 35065.109 | 36413.77 | 32367.793 | -17532.555 | -18881.213 | -13486.581 | 227.238 | 227.669 | 230.345 | 49.995
2025-10-22 00:34 | 78222.172 | 90360.094 | -44505.715 | 0.86 | 0.86567 | 26973.162 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -17532.555 | -12137.923 | 227.756 | 228.295 | 230.539 | 49.985
2025-10-22 00:35 | 82268.141 | 95754.727 | -48551.691 | 0.86 | 0.85915 | 28321.82 | 26973.162 | 26973.162 | 33716.453 | 32367.793 | 29670.479 | -17532.555 | -17532.555 | -13486.581 | 228.123 | 229.094 | 230.604 | 49.978
2025-10-22 00:36 | 75524.852 | 89011.43 | -45854.375 | 0.85 | 0.84848 | 26973.162 | 24275.846 | 24275.846 | 31019.137 | 31019.137 | 26973.162 | -16183.896 | -17532.555 | -12137.923 | 228.123 | 229.245 | 230.475 | 49.989
2025-10-22 00:37 | 78222.172 | 90360.094 | -44505.715 | 0.86 | 0.86567 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 227.54 | 228.533 | 229.892 | 49.997
2025-10-22 00:38 | 72827.539 | 83616.805 | -40459.742 | 0.87 | 0.87097 | 25624.504 | 22927.188 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -12137.923 | 227.173 | 228.015 | 229.374 | 50.003
2025-10-22 00:39 | 75524.852 | 86314.117 | -41808.402 | 0.87 | 0.875 | 26973.162 | 22927.188 | 25624.504 | 31019.137 | 26973.162 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 226.698 | 227.173 | 228.835 | 50.002
2025-10-22 00:40 | 86314.117 | 98452.039 | -47203.031 | 0.87 | 0.87671 | 31019.137 | 25624.504 | 28321.82 | 35065.109 | 31019.137 | 32367.793 | -17532.555 | -16183.896 | -13486.581 | 227.41 | 228.166 | 229.763 | 49.989
2025-10-22 00:41 | 80919.484 | 93057.406 | -44505.715 | 0.87 | 0.86957 | 29670.479 | 24275.846 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 227.346 | 228.317 | 229.525 | 50.003
2025-10-22 00:42 | 78222.172 | 89011.43 | -43157.059 | 0.87 | 0.87879 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 227.259 | 228.36 | 229.525 | 50.008
2025-10-22 00:43 | 74176.195 | 86314.117 | -41808.402 | 0.87 | 0.85938 | 26973.162 | 22927.188 | 25624.504 | 31019.137 | 26973.162 | 28321.82 | -16183.896 | -14835.239 | -10789.265 | 227.216 | 228.209 | 229.504 | 50.01
2025-10-22 00:44 | 72827.539 | 84965.461 | -43157.059 | 0.85 | 0.85714 | 26973.162 | 21578.529 | 24275.846 | 31019.137 | 26973.162 | 26973.162 | -16183.896 | -16183.896 | -12137.923 | 226.763 | 227.324 | 229.051 | 50.018
2025-10-22 00:45 | 68781.563 | 80919.484 | -40459.742 | 0.86 | 0.85 | 25624.504 | 20229.871 | 22927.188 | 29670.479 | 25624.504 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 226.849 | 227.454 | 229.072 | 50.018
2025-10-22 00:46 | 70130.219 | 80919.484 | -39111.086 | 0.87 | 0.86667 | 24275.846 | 21578.529 | 24275.846 | 28321.82 | 25624.504 | 25624.504 | -14835.239 | -13486.581 | -10789.265 | 226.957 | 227.669 | 229.18 | 49.992
2025-10-22 00:47 | 72827.539 | 82268.141 | -39111.086 | 0.88 | 0.88525 | 25624.504 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 227.864 | 228.619 | 230.194 | 49.989
2025-10-22 00:48 | 76873.508 | 89011.43 | -43157.059 | 0.87 | 0.86364 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 226.742 | 227.367 | 229.18 | 49.996
2025-10-22 00:49 | 78222.172 | 90360.094 | -43157.059 | 0.87 | 0.86567 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.569 | 227.022 | 229.051 | 49.99
2025-10-22 00:50 | 74176.195 | 86314.117 | -43157.059 | 0.86 | 0.85938 | 25624.504 | 24275.846 | 24275.846 | 31019.137 | 28321.82 | 26973.162 | -16183.896 | -16183.896 | -10789.265 | 227.022 | 227.562 | 229.245 | 50.009
2025-10-22 00:51 | 84965.461 | 95754.727 | -44505.715 | 0.88 | 0.88732 | 29670.479 | 26973.162 | 26973.162 | 33716.453 | 32367.793 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 226.439 | 227.195 | 228.792 | 50.019
2025-10-22 00:52 | 79570.828 | 91708.75 | -44505.715 | 0.87 | 0.86765 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 227.605 | 228.295 | 229.935 | 50.019
2025-10-22 00:53 | 86314.117 | 98452.039 | -45854.375 | 0.88 | 0.87671 | 29670.479 | 28321.82 | 28321.82 | 35065.109 | 32367.793 | 31019.137 | -16183.896 | -17532.555 | -12137.923 | 226.569 | 227.087 | 228.899 | 49.995
2025-10-22 00:54 | 74176.195 | 84965.461 | -40459.742 | 0.87 | 0.87302 | 26973.162 | 24275.846 | 24275.846 | 31019.137 | 28321.82 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 225.49 | 226.137 | 227.972 | 50.012
2025-10-22 00:55 | 71478.875 | 83616.805 | -41808.402 | 0.86 | 0.85484 | 25624.504 | 21578.529 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -12137.923 | 226.936 | 227.734 | 229.202 | 50.004
2025-10-22 00:56 | 72827.539 | 83616.805 | -40459.742 | 0.87 | 0.87097 | 26973.162 | 22927.188 | 24275.846 | 31019.137 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 226.612 | 227.497 | 228.964 | 49.98
2025-10-22 00:57 | 63386.93 | 72827.539 | -33716.453 | 0.88 | 0.87037 | 21578.529 | 20229.871 | 21578.529 | 25624.504 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 225.986 | 227.044 | 228.317 | 49.976
2025-10-22 00:58 | 49900.348 | 56643.641 | -28321.82 | 0.87 | 0.88095 | 17532.555 | 16183.896 | 16183.896 | 20229.871 | 18881.213 | 18881.213 | -9440.606 | -9440.606 | -8091.948 | 227.885 | 228.986 | 229.763 | 49.993
2025-10-22 00:59 | 43157.059 | 51249.008 | -25624.504 | 0.85 | 0.84211 | 14835.239 | 13486.581 | 14835.239 | 17532.555 | 16183.896 | 16183.896 | -9440.606 | -9440.606 | -8091.948 | 229.914 | 230.993 | 231.467 | 50.001
2025-10-22 01:00 | 40459.742 | 47203.031 | -24275.846 | 0.86 | 0.85714 | 14835.239 | 13486.581 | 13486.581 | 16183.896 | 16183.896 | 14835.239 | -8091.948 | -8091.948 | -6743.291 | 231.208 | 232.244 | 232.87 | 50.005
2025-10-22 01:01 | 41808.402 | 47203.031 | -22927.188 | 0.88 | 0.88571 | 13486.581 | 13486.581 | 13486.581 | 16183.896 | 16183.896 | 16183.896 | -8091.948 | -6743.291 | -8091.948 | 231.921 | 232.654 | 233.28 | 49.999
2025-10-22 01:02 | 41808.402 | 48551.691 | -22927.188 | 0.87 | 0.86111 | 13486.581 | 14835.239 | 13486.581 | 16183.896 | 17532.555 | 16183.896 | -8091.948 | -8091.948 | -6743.291 | 231.208 | 231.489 | 232.676 | 49.978
2025-10-22 01:03 | 43157.059 | 49900.348 | -24275.846 | 0.87 | 0.86486 | 13486.581 | 16183.896 | 13486.581 | 16183.896 | 17532.555 | 16183.896 | -8091.948 | -9440.606 | -6743.291 | 232.028 | 232.244 | 233.517 | 49.983
2025-10-22 01:04 | 44505.715 | 51249.008 | -25624.504 | 0.86 | 0.86842 | 13486.581 | 17532.555 | 13486.581 | 16183.896 | 18881.213 | 16183.896 | -8091.948 | -9440.606 | -8091.948 | 232.546 | 233.021 | 234.035 | 49.982
2025-10-22 01:05 | 44505.715 | 51249.008 | -25624.504 | 0.86 | 0.86842 | 13486.581 | 17532.555 | 13486.581 | 14835.239 | 20229.871 | 14835.239 | -8091.948 | -9440.606 | -8091.948 | 233.453 | 233.776 | 234.963 | 49.98
2025-10-22 01:06 | 44505.715 | 51249.008 | -24275.846 | 0.86 | 0.86842 | 13486.581 | 17532.555 | 13486.581 | 14835.239 | 20229.871 | 14835.239 | -8091.948 | -9440.606 | -6743.291 | 233.561 | 233.884 | 234.747 | 49.982
2025-10-22 01:07 | 44505.715 | 51249.008 | -24275.846 | 0.87 | 0.86842 | 13486.581 | 17532.555 | 13486.581 | 14835.239 | 20229.871 | 16183.896 | -8091.948 | -9440.606 | -8091.948 | 232.784 | 233.237 | 233.927 | 49.987
2025-10-22 01:08 | 44505.715 | 51249.008 | -24275.846 | 0.87 | 0.86842 | 13486.581 | 17532.555 | 13486.581 | 14835.239 | 20229.871 | 14835.239 | -8091.948 | -9440.606 | -6743.291 | 233.431 | 234.057 | 234.488 | 50.006
2025-10-22 01:09 | 40459.742 | 47203.031 | -22927.188 | 0.87 | 0.85714 | 13486.581 | 14835.239 | 13486.581 | 14835.239 | 16183.896 | 16183.896 | -8091.948 | -8091.948 | -8091.948 | 233.151 | 234.661 | 234.078 | 49.997
2025-10-22 01:10 | 41808.402 | 48551.691 | -24275.846 | 0.87 | 0.86111 | 13486.581 | 14835.239 | 13486.581 | 16183.896 | 16183.896 | 16183.896 | -8091.948 | -8091.948 | -8091.948 | 232.46 | 233.82 | 233.496 | 50.003
2025-10-22 01:11 | 40459.742 | 45854.375 | -21578.529 | 0.88 | 0.88235 | 13486.581 | 13486.581 | 13486.581 | 14835.239 | 16183.896 | 14835.239 | -6743.291 | -6743.291 | -8091.948 | 232.568 | 233.884 | 233.668 | 50.008
2025-10-22 01:12 | 39111.086 | 44505.715 | -20229.871 | 0.88 | 0.87879 | 12137.923 | 13486.581 | 12137.923 | 14835.239 | 14835.239 | 14835.239 | -6743.291 | -6743.291 | -6743.291 | 233.086 | 234.747 | 233.992 | 50.011
2025-10-22 01:13 | 40459.742 | 45854.375 | -21578.529 | 0.88 | 0.88235 | 13486.581 | 13486.581 | 13486.581 | 14835.239 | 16183.896 | 14835.239 | -6743.291 | -6743.291 | -6743.291 | 232.633 | 234.575 | 233.582 | 49.999
2025-10-22 01:14 | 40459.742 | 45854.375 | -21578.529 | 0.88 | 0.88235 | 13486.581 | 13486.581 | 13486.581 | 14835.239 | 16183.896 | 14835.239 | -6743.291 | -6743.291 | -6743.291 | 232.374 | 234.424 | 233.582 | 50.006
2025-10-22 01:15 | 40459.742 | 44505.715 | -21578.529 | 0.88 | 0.90909 | 13486.581 | 13486.581 | 13486.581 | 14835.239 | 14835.239 | 14835.239 | -8091.948 | -6743.291 | -6743.291 | 233.129 | 234.445 | 234.337 | 50.015
2025-10-22 01:16 | 40459.742 | 45854.375 | -21578.529 | 0.88 | 0.88235 | 13486.581 | 13486.581 | 13486.581 | 14835.239 | 14835.239 | 16183.896 | -8091.948 | -6743.291 | -6743.291 | 233.086 | 234.294 | 234.186 | 50.021
2025-10-22 01:17 | 41808.402 | 48551.691 | -22927.188 | 0.87 | 0.86111 | 13486.581 | 14835.239 | 14835.239 | 16183.896 | 16183.896 | 16183.896 | -8091.948 | -8091.948 | -8091.948 | 232.87 | 234.294 | 234.057 | 50.012
2025-10-22 01:18 | 41808.402 | 47203.031 | -22927.188 | 0.88 | 0.88571 | 13486.581 | 13486.581 | 14835.239 | 16183.896 | 16183.896 | 16183.896 | -8091.948 | -6743.291 | -8091.948 | 232.525 | 233.863 | 233.712 | 50.015
2025-10-22 01:19 | 40459.742 | 47203.031 | -21578.529 | 0.88 | 0.85714 | 13486.581 | 13486.581 | 13486.581 | 14835.239 | 14835.239 | 16183.896 | -8091.948 | -6743.291 | -6743.291 | 232.417 | 233.82 | 233.582 | 50.003
2025-10-22 01:20 | 41808.402 | 47203.031 | -22927.188 | 0.88 | 0.88571 | 13486.581 | 13486.581 | 14835.239 | 14835.239 | 14835.239 | 16183.896 | -8091.948 | -6743.291 | -6743.291 | 233.172 | 234.683 | 234.467 | 49.994
2025-10-22 01:21 | 39111.086 | 44505.715 | -20229.871 | 0.89 | 0.87879 | 13486.581 | 13486.581 | 13486.581 | 14835.239 | 14835.239 | 14835.239 | -6743.291 | -6743.291 | -6743.291 | 233.258 | 234.704 | 234.575 | 49.996
2025-10-22 01:22 | 40459.742 | 45854.375 | -21578.529 | 0.89 | 0.88235 | 13486.581 | 13486.581 | 13486.581 | 14835.239 | 14835.239 | 16183.896 | -8091.948 | -6743.291 | -6743.291 | 233.388 | 234.683 | 234.575 | 50.008
2025-10-22 01:23 | 41808.402 | 47203.031 | -21578.529 | 0.88 | 0.88571 | 13486.581 | 13486.581 | 14835.239 | 14835.239 | 16183.896 | 16183.896 | -8091.948 | -6743.291 | -6743.291 | 233.129 | 234.445 | 234.424 | 50.006
2025-10-22 01:24 | 43157.059 | 48551.691 | -21578.529 | 0.89 | 0.88889 | 13486.581 | 14835.239 | 14835.239 | 14835.239 | 17532.555 | 16183.896 | -8091.948 | -8091.948 | -6743.291 | 233.41 | 234.553 | 234.855 | 50.02
2025-10-22 01:25 | 43157.059 | 49900.348 | -22927.188 | 0.88 | 0.86486 | 13486.581 | 16183.896 | 14835.239 | 16183.896 | 17532.555 | 16183.896 | -8091.948 | -8091.948 | -6743.291 | 233.388 | 234.424 | 234.747 | 50.021
2025-10-22 01:26 | 43157.059 | 48551.691 | -22927.188 | 0.88 | 0.88889 | 13486.581 | 14835.239 | 13486.581 | 14835.239 | 17532.555 | 16183.896 | -8091.948 | -8091.948 | -6743.291 | 233.971 | 234.898 | 235.179 | 50.02
2025-10-22 01:27 | 40459.742 | 45854.375 | -21578.529 | 0.89 | 0.88235 | 12137.923 | 14835.239 | 13486.581 | 14835.239 | 16183.896 | 14835.239 | -6743.291 | -8091.948 | -6743.291 | 234.51 | 235.416 | 235.589 | 50.014
2025-10-22 01:28 | 41808.402 | 47203.031 | -21578.529 | 0.89 | 0.88571 | 13486.581 | 14835.239 | 13486.581 | 14835.239 | 17532.555 | 14835.239 | -6743.291 | -8091.948 | -6743.291 | 233.69 | 234.64 | 234.791 | 50.007
2025-10-22 01:29 | 41808.402 | 45854.375 | -21578.529 | 0.88 | 0.91176 | 13486.581 | 14835.239 | 13486.581 | 14835.239 | 16183.896 | 14835.239 | -6743.291 | -8091.948 | -6743.291 | 233.625 | 234.532 | 234.704 | 49.999
2025-10-22 01:30 | 39111.086 | 44505.715 | -20229.871 | 0.89 | 0.87879 | 13486.581 | 13486.581 | 13486.581 | 14835.239 | 14835.239 | 14835.239 | -6743.291 | -6743.291 | -6743.291 | 234.057 | 234.985 | 234.985 | 50.011
2025-10-22 01:31 | 39111.086 | 43157.059 | -20229.871 | 0.89 | 0.90625 | 12137.923 | 13486.581 | 13486.581 | 14835.239 | 14835.239 | 14835.239 | -6743.291 | -6743.291 | -6743.291 | 233.884 | 234.64 | 234.532 | 50.002
2025-10-22 01:32 | 41808.402 | 47203.031 | -21578.529 | 0.89 | 0.88571 | 13486.581 | 14835.239 | 13486.581 | 14835.239 | 16183.896 | 16183.896 | -6743.291 | -8091.948 | -6743.291 | 230.518 | 231.295 | 231.467 | 49.999
2025-10-22 01:33 | 44505.715 | 49900.348 | -22927.188 | 0.88 | 0.89189 | 13486.581 | 16183.896 | 13486.581 | 14835.239 | 18881.213 | 16183.896 | -6743.291 | -8091.948 | -6743.291 | 229.827 | 230.712 | 231.144 | 50.008
2025-10-22 01:34 | 41808.402 | 47203.031 | -21578.529 | 0.89 | 0.88571 | 13486.581 | 16183.896 | 13486.581 | 14835.239 | 17532.555 | 14835.239 | -6743.291 | -8091.948 | -6743.291 | 229.676 | 230.518 | 230.561 | 49.999
2025-10-22 01:35 | 41808.402 | 47203.031 | -21578.529 | 0.89 | 0.88571 | 13486.581 | 16183.896 | 13486.581 | 14835.239 | 17532.555 | 14835.239 | -6743.291 | -8091.948 | -6743.291 | 229.266 | 230.065 | 230.194 | 49.994
2025-10-22 01:36 | 41808.402 | 47203.031 | -21578.529 | 0.89 | 0.88571 | 13486.581 | 16183.896 | 13486.581 | 14835.239 | 17532.555 | 14835.239 | -6743.291 | -8091.948 | -6743.291 | 230.216 | 230.906 | 231.316 | 49.993
2025-10-22 01:37 | 41808.402 | 47203.031 | -21578.529 | 0.89 | 0.88571 | 13486.581 | 14835.239 | 13486.581 | 14835.239 | 17532.555 | 14835.239 | -6743.291 | -8091.948 | -6743.291 | 230.237 | 230.949 | 231.467 | 49.986
2025-10-22 01:38 | 41808.402 | 47203.031 | -21578.529 | 0.89 | 0.88571 | 13486.581 | 16183.896 | 13486.581 | 14835.239 | 17532.555 | 14835.239 | -6743.291 | -8091.948 | -6743.291 | 230.302 | 230.647 | 231.359 | 50.009
2025-10-22 01:39 | 44505.715 | 49900.348 | -22927.188 | 0.89 | 0.89189 | 13486.581 | 16183.896 | 14835.239 | 16183.896 | 18881.213 | 16183.896 | -8091.948 | -8091.948 | -6743.291 | 230.065 | 230.453 | 231.208 | 49.998
2025-10-22 01:40 | 47203.031 | 52597.664 | -24275.846 | 0.88 | 0.89744 | 14835.239 | 17532.555 | 14835.239 | 17532.555 | 18881.213 | 17532.555 | -8091.948 | -8091.948 | -8091.948 | 230 | 230.777 | 231.424 | 50.003
2025-10-22 01:41 | 51249.008 | 57992.297 | -26973.162 | 0.89 | 0.88372 | 16183.896 | 18881.213 | 16183.896 | 18881.213 | 20229.871 | 18881.213 | -8091.948 | -9440.606 | -8091.948 | 229.029 | 229.763 | 231.079 | 50.008
2025-10-22 01:42 | 57992.297 | 64735.586 | -28321.82 | 0.9 | 0.89583 | 18881.213 | 20229.871 | 18881.213 | 20229.871 | 22927.188 | 20229.871 | -9440.606 | -9440.606 | -9440.606 | 228.792 | 229.417 | 230.777 | 50.016
2025-10-22 01:43 | 51249.008 | 59340.957 | -29670.479 | 0.87 | 0.86364 | 17532.555 | 17532.555 | 16183.896 | 20229.871 | 20229.871 | 18881.213 | -10789.265 | -10789.265 | -8091.948 | 228.252 | 228.878 | 230.216 | 50.011
2025-10-22 01:44 | 59340.957 | 67432.906 | -32367.793 | 0.88 | 0.88 | 20229.871 | 18881.213 | 20229.871 | 24275.846 | 22927.188 | 21578.529 | -10789.265 | -10789.265 | -9440.606 | 227.475 | 228.252 | 229.417 | 50.016
2025-10-22 01:45 | 60689.613 | 70130.219 | -32367.793 | 0.88 | 0.86538 | 21578.529 | 20229.871 | 20229.871 | 24275.846 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 227.281 | 228.036 | 229.266 | 50.015
2025-10-22 01:46 | 63386.93 | 71478.875 | -33716.453 | 0.88 | 0.88679 | 21578.529 | 20229.871 | 21578.529 | 25624.504 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 227.281 | 227.907 | 229.245 | 50
2025-10-22 01:47 | 64735.586 | 74176.195 | -35065.109 | 0.88 | 0.87273 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 227.238 | 227.95 | 229.266 | 50.002
2025-10-22 01:48 | 63386.93 | 72827.539 | -36413.77 | 0.87 | 0.87037 | 21578.529 | 20229.871 | 20229.871 | 25624.504 | 24275.846 | 22927.188 | -12137.923 | -12137.923 | -10789.265 | 226.914 | 227.907 | 228.813 | 49.986
2025-10-22 01:49 | 64735.586 | 74176.195 | -35065.109 | 0.88 | 0.87273 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 226.893 | 227.95 | 228.943 | 49.99
2025-10-22 01:50 | 64735.586 | 74176.195 | -35065.109 | 0.88 | 0.87273 | 22927.188 | 21578.529 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 227 | 228.015 | 228.727 | 49.991
2025-10-22 01:51 | 64735.586 | 72827.539 | -35065.109 | 0.88 | 0.88889 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 226.698 | 227.626 | 228.317 | 49.994
2025-10-22 01:52 | 64735.586 | 72827.539 | -35065.109 | 0.88 | 0.88889 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 226.979 | 227.864 | 228.619 | 50.009
2025-10-22 01:53 | 59340.957 | 67432.906 | -32367.793 | 0.87 | 0.88 | 20229.871 | 18881.213 | 18881.213 | 22927.188 | 21578.529 | 21578.529 | -10789.265 | -12137.923 | -9440.606 | 224.066 | 224.929 | 225.727 | 50.013
2025-10-22 01:54 | 66084.242 | 74176.195 | -33716.453 | 0.89 | 0.89091 | 22927.188 | 21578.529 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 223.159 | 224.217 | 224.907 | 50.008
2025-10-22 01:55 | 66084.242 | 75524.852 | -33716.453 | 0.89 | 0.875 | 22927.188 | 21578.529 | 22927.188 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 222.944 | 224.044 | 224.67 | 50.017
2025-10-22 01:56 | 62038.273 | 70130.219 | -31019.137 | 0.9 | 0.88462 | 21578.529 | 20229.871 | 21578.529 | 24275.846 | 22927.188 | 22927.188 | -10789.265 | -10789.265 | -9440.606 | 222.9 | 224.066 | 224.584 | 50.019
2025-10-22 01:57 | 63386.93 | 70130.219 | -31019.137 | 0.89 | 0.90385 | 21578.529 | 20229.871 | 21578.529 | 24275.846 | 22927.188 | 22927.188 | -10789.265 | -10789.265 | -9440.606 | 223.483 | 224.584 | 225.209 | 50.026
2025-10-22 01:58 | 64735.586 | 72827.539 | -32367.793 | 0.89 | 0.88889 | 21578.529 | 21578.529 | 21578.529 | 24275.846 | 24275.846 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 222.749 | 223.634 | 224.692 | 50.026
2025-10-22 01:59 | 63386.93 | 72827.539 | -33716.453 | 0.89 | 0.87037 | 21578.529 | 21578.529 | 21578.529 | 24275.846 | 24275.846 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 224.476 | 225.317 | 226.483 | 50.036
2025-10-22 02:00 | 64735.586 | 74176.195 | -36413.77 | 0.87 | 0.87273 | 21578.529 | 22927.188 | 20229.871 | 24275.846 | 26973.162 | 22927.188 | -12137.923 | -13486.581 | -9440.606 | 227.022 | 227.389 | 229.072 | 50.029
2025-10-22 02:01 | 62038.273 | 71478.875 | -35065.109 | 0.86 | 0.86792 | 20229.871 | 21578.529 | 18881.213 | 24275.846 | 25624.504 | 21578.529 | -12137.923 | -13486.581 | -9440.606 | 226.871 | 226.957 | 228.382 | 49.994
2025-10-22 02:02 | 64735.586 | 75524.852 | -37762.426 | 0.86 | 0.85714 | 21578.529 | 22927.188 | 20229.871 | 25624.504 | 26973.162 | 22927.188 | -13486.581 | -14835.239 | -10789.265 | 226.439 | 226.461 | 228.123 | 49.969
2025-10-22 02:03 | 62038.273 | 70130.219 | -33716.453 | 0.87 | 0.88462 | 20229.871 | 22927.188 | 20229.871 | 22927.188 | 25624.504 | 21578.529 | -10789.265 | -12137.923 | -9440.606 | 227.173 | 227.367 | 228.813 | 49.971
2025-10-22 02:04 | 64735.586 | 74176.195 | -35065.109 | 0.87 | 0.87273 | 21578.529 | 21578.529 | 21578.529 | 25624.504 | 25624.504 | 22927.188 | -12137.923 | -13486.581 | -9440.606 | 226.893 | 227.324 | 228.36 | 49.986
2025-10-22 02:05 | 64735.586 | 74176.195 | -35065.109 | 0.88 | 0.87273 | 21578.529 | 21578.529 | 21578.529 | 25624.504 | 25624.504 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 227.475 | 227.972 | 228.813 | 50.009
2025-10-22 02:06 | 62038.273 | 70130.219 | -32367.793 | 0.88 | 0.88462 | 21578.529 | 20229.871 | 21578.529 | 24275.846 | 22927.188 | 22927.188 | -12137.923 | -10789.265 | -9440.606 | 226.483 | 227.259 | 228.23 | 50.002
2025-10-22 02:07 | 59340.957 | 67432.906 | -32367.793 | 0.87 | 0.88 | 20229.871 | 18881.213 | 20229.871 | 24275.846 | 21578.529 | 21578.529 | -12137.923 | -10789.265 | -9440.606 | 224.778 | 225.684 | 227.044 | 50.007
2025-10-22 02:08 | 62038.273 | 70130.219 | -32367.793 | 0.88 | 0.88462 | 21578.529 | 20229.871 | 20229.871 | 24275.846 | 22927.188 | 22927.188 | -12137.923 | -10789.265 | -9440.606 | 225.058 | 225.857 | 227.259 | 50.017
2025-10-22 02:09 | 63386.93 | 72827.539 | -33716.453 | 0.88 | 0.87037 | 21578.529 | 20229.871 | 21578.529 | 25624.504 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -10789.265 | 224.864 | 225.49 | 227 | 50.018
2025-10-22 02:10 | 64735.586 | 72827.539 | -33716.453 | 0.88 | 0.88889 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 225.166 | 225.555 | 227.367 | 50.002
2025-10-22 02:11 | 60689.613 | 68781.563 | -32367.793 | 0.88 | 0.88235 | 21578.529 | 18881.213 | 20229.871 | 24275.846 | 22927.188 | 22927.188 | -10789.265 | -10789.265 | -9440.606 | 225.706 | 226.137 | 227.993 | 50.009
2025-10-22 02:12 | 62038.273 | 70130.219 | -32367.793 | 0.88 | 0.88462 | 21578.529 | 20229.871 | 20229.871 | 24275.846 | 22927.188 | 22927.188 | -10789.265 | -10789.265 | -9440.606 | 225.102 | 225.555 | 227.216 | 50.016
2025-10-22 02:13 | 62038.273 | 70130.219 | -33716.453 | 0.88 | 0.88462 | 21578.529 | 20229.871 | 20229.871 | 24275.846 | 24275.846 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 225.166 | 225.576 | 227.238 | 50.022
2025-10-22 02:14 | 63386.93 | 71478.875 | -33716.453 | 0.88 | 0.88679 | 21578.529 | 21578.529 | 20229.871 | 24275.846 | 24275.846 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 225.49 | 225.9 | 227.497 | 50.019
2025-10-22 02:15 | 63386.93 | 71478.875 | -33716.453 | 0.88 | 0.88679 | 21578.529 | 21578.529 | 20229.871 | 24275.846 | 24275.846 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 225.943 | 226.202 | 227.993 | 50.026
2025-10-22 02:16 | 66084.242 | 75524.852 | -36413.77 | 0.87 | 0.875 | 22927.188 | 21578.529 | 21578.529 | 25624.504 | 25624.504 | 24275.846 | -12137.923 | -13486.581 | -10789.265 | 226.094 | 226.288 | 228.187 | 50.022
2025-10-22 02:17 | 63386.93 | 72827.539 | -36413.77 | 0.87 | 0.87037 | 21578.529 | 21578.529 | 20229.871 | 25624.504 | 25624.504 | 22927.188 | -12137.923 | -13486.581 | -10789.265 | 225.835 | 226.202 | 227.885 | 50.019
2025-10-22 02:18 | 60689.613 | 68781.563 | -33716.453 | 0.87 | 0.88235 | 20229.871 | 20229.871 | 20229.871 | 24275.846 | 22927.188 | 21578.529 | -12137.923 | -12137.923 | -9440.606 | 226.655 | 227.13 | 228.792 | 50.033
2025-10-22 02:19 | 59340.957 | 67432.906 | -32367.793 | 0.88 | 0.88 | 20229.871 | 18881.213 | 20229.871 | 22927.188 | 21578.529 | 21578.529 | -10789.265 | -10789.265 | -9440.606 | 226.849 | 227.713 | 228.943 | 50.024
2025-10-22 02:20 | 57992.297 | 64735.586 | -28321.82 | 0.89 | 0.89583 | 18881.213 | 18881.213 | 18881.213 | 21578.529 | 21578.529 | 21578.529 | -9440.606 | -9440.606 | -9440.606 | 227.367 | 228.036 | 229.029 | 50.025
2025-10-22 02:21 | 57992.297 | 64735.586 | -29670.479 | 0.89 | 0.89583 | 18881.213 | 18881.213 | 18881.213 | 21578.529 | 21578.529 | 21578.529 | -9440.606 | -9440.606 | -10789.265 | 227.605 | 228.295 | 229.029 | 50.024
2025-10-22 02:22 | 62038.273 | 71478.875 | -33716.453 | 0.88 | 0.86792 | 21578.529 | 20229.871 | 20229.871 | 24275.846 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -10789.265 | 227.346 | 228.058 | 228.835 | 50.009
2025-10-22 02:23 | 62038.273 | 71478.875 | -35065.109 | 0.87 | 0.86792 | 21578.529 | 20229.871 | 20229.871 | 24275.846 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -10789.265 | 226.871 | 227.518 | 228.425 | 50.018
2025-10-22 02:24 | 64735.586 | 75524.852 | -36413.77 | 0.87 | 0.85714 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -13486.581 | -13486.581 | -10789.265 | 227.324 | 227.799 | 228.835 | 50.02
2025-10-22 02:25 | 62038.273 | 71478.875 | -33716.453 | 0.88 | 0.86792 | 21578.529 | 20229.871 | 20229.871 | 24275.846 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 227.044 | 227.54 | 228.511 | 50.018
2025-10-22 02:26 | 71478.875 | 80919.484 | -37762.426 | 0.88 | 0.88333 | 25624.504 | 21578.529 | 24275.846 | 28321.82 | 25624.504 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 226.698 | 227.475 | 228.662 | 50.019
2025-10-22 02:27 | 75524.852 | 87662.773 | -43157.059 | 0.86 | 0.86154 | 26973.162 | 22927.188 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.418 | 227.432 | 228.619 | 50.014
2025-10-22 02:28 | 67432.906 | 78222.172 | -40459.742 | 0.85 | 0.86207 | 24275.846 | 20229.871 | 22927.188 | 28321.82 | 25624.504 | 24275.846 | -14835.239 | -14835.239 | -10789.265 | 227.259 | 228.23 | 229.353 | 50.009
2025-10-22 02:29 | 78222.172 | 89011.43 | -43157.059 | 0.87 | 0.87879 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -14835.239 | -16183.896 | -12137.923 | 226.288 | 226.979 | 228.748 | 50
2025-10-22 02:30 | 86314.117 | 99800.695 | -48551.691 | 0.87 | 0.86486 | 29670.479 | 28321.82 | 28321.82 | 35065.109 | 33716.453 | 31019.137 | -17532.555 | -17532.555 | -13486.581 | 226.439 | 226.914 | 229.158 | 49.999
2025-10-22 02:31 | 87662.773 | 101149.359 | -49900.348 | 0.87 | 0.86667 | 29670.479 | 28321.82 | 28321.82 | 35065.109 | 33716.453 | 31019.137 | -17532.555 | -18881.213 | -13486.581 | 226.504 | 226.914 | 229.137 | 49.995
2025-10-22 02:32 | 84965.461 | 97103.383 | -45854.375 | 0.87 | 0.875 | 29670.479 | 28321.82 | 26973.162 | 33716.453 | 32367.793 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 226.029 | 226.677 | 228.619 | 49.977
2025-10-22 02:33 | 79570.828 | 91708.75 | -44505.715 | 0.87 | 0.86765 | 26973.162 | 26973.162 | 25624.504 | 32367.793 | 32367.793 | 28321.82 | -16183.896 | -17532.555 | -12137.923 | 226.051 | 226.569 | 228.662 | 49.992
2025-10-22 02:34 | 86314.117 | 98452.039 | -48551.691 | 0.87 | 0.87671 | 29670.479 | 29670.479 | 26973.162 | 33716.453 | 35065.109 | 29670.479 | -17532.555 | -18881.213 | -13486.581 | 225.986 | 226.483 | 228.705 | 49.999
2025-10-22 02:35 | 84965.461 | 97103.383 | -47203.031 | 0.87 | 0.875 | 28321.82 | 28321.82 | 26973.162 | 33716.453 | 33716.453 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 225.296 | 226.116 | 227.885 | 49.995
2025-10-22 02:36 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 28321.82 | 26973.162 | 26973.162 | 33716.453 | 32367.793 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.145 | 226.418 | 227.626 | 50.013
2025-10-22 02:37 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 28321.82 | 26973.162 | 26973.162 | 33716.453 | 32367.793 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.799 | 226.051 | 227.238 | 50.01
2025-10-22 02:38 | 83616.805 | 95754.727 | -45854.375 | 0.87 | 0.87324 | 29670.479 | 26973.162 | 26973.162 | 33716.453 | 32367.793 | 29670.479 | -16183.896 | -17532.555 | -13486.581 | 224.044 | 225.425 | 226.461 | 50.019
2025-10-22 02:39 | 80919.484 | 93057.406 | -45854.375 | 0.86 | 0.86957 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 224.476 | 225.641 | 227.022 | 50.003
2025-10-22 02:40 | 80919.484 | 93057.406 | -44505.715 | 0.87 | 0.86957 | 28321.82 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.778 | 225.986 | 227.238 | 50.01
2025-10-22 02:41 | 80919.484 | 91708.75 | -43157.059 | 0.88 | 0.88235 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 224.778 | 225.727 | 227.324 | 50.004
2025-10-22 02:42 | 80919.484 | 93057.406 | -44505.715 | 0.87 | 0.86957 | 28321.82 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.231 | 226.288 | 227.777 | 50.013
2025-10-22 02:43 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 31019.137 | -16183.896 | -16183.896 | -12137.923 | 225.231 | 226.245 | 227.691 | 50.001
2025-10-22 02:44 | 75524.852 | 86314.117 | -43157.059 | 0.86 | 0.875 | 26973.162 | 22927.188 | 25624.504 | 31019.137 | 26973.162 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 225.253 | 226.267 | 227.82 | 50.012
2025-10-22 02:45 | 80919.484 | 93057.406 | -44505.715 | 0.87 | 0.86957 | 28321.82 | 24275.846 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.576 | 226.806 | 228.252 | 50.02
2025-10-22 02:46 | 82268.141 | 94406.063 | -44505.715 | 0.88 | 0.87143 | 29670.479 | 25624.504 | 28321.82 | 33716.453 | 29670.479 | 31019.137 | -16183.896 | -16183.896 | -12137.923 | 225.102 | 226.526 | 227.691 | 50.021
2025-10-22 02:47 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 31019.137 | -16183.896 | -16183.896 | -13486.581 | 224.433 | 225.792 | 226.871 | 50.019
2025-10-22 02:48 | 82268.141 | 93057.406 | -43157.059 | 0.88 | 0.88406 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.174 | 225.382 | 226.698 | 50.023
2025-10-22 02:49 | 76873.508 | 89011.43 | -43157.059 | 0.87 | 0.86364 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 224.692 | 225.814 | 227.216 | 50.024
2025-10-22 02:50 | 78222.172 | 90360.094 | -43157.059 | 0.87 | 0.86567 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 224.95 | 225.835 | 227.432 | 50.019
2025-10-22 02:51 | 80919.484 | 93057.406 | -44505.715 | 0.88 | 0.86957 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.648 | 225.684 | 227.13 | 50.007
2025-10-22 02:52 | 82268.141 | 94406.063 | -44505.715 | 0.87 | 0.87143 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.015 | 226.116 | 227.562 | 50.006
2025-10-22 02:53 | 84965.461 | 98452.039 | -47203.031 | 0.87 | 0.86301 | 29670.479 | 28321.82 | 28321.82 | 33716.453 | 32367.793 | 31019.137 | -16183.896 | -17532.555 | -13486.581 | 225.188 | 226.245 | 227.799 | 50.015
2025-10-22 02:54 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 224.778 | 225.835 | 227.324 | 50.036
2025-10-22 02:55 | 76873.508 | 89011.43 | -44505.715 | 0.87 | 0.86364 | 26973.162 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 224.692 | 225.857 | 227.173 | 50.038
2025-10-22 02:56 | 79570.828 | 91708.75 | -44505.715 | 0.87 | 0.86765 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.389 | 225.533 | 226.806 | 50.03
2025-10-22 02:57 | 78222.172 | 89011.43 | -43157.059 | 0.87 | 0.87879 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 224.994 | 226.18 | 227.41 | 50.035
2025-10-22 02:58 | 80919.484 | 93057.406 | -44505.715 | 0.87 | 0.86957 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.799 | 225.986 | 227.195 | 50.031
2025-10-22 02:59 | 79570.828 | 90360.094 | -43157.059 | 0.87 | 0.8806 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.404 | 226.375 | 227.518 | 50.026
2025-10-22 03:00 | 76873.508 | 89011.43 | -43157.059 | 0.87 | 0.86364 | 26973.162 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 225.77 | 226.698 | 227.864 | 50.022
2025-10-22 03:01 | 79570.828 | 91708.75 | -44505.715 | 0.87 | 0.86765 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.684 | 226.785 | 227.95 | 49.999
2025-10-22 03:02 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 32367.793 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 225.857 | 226.569 | 228.403 | 49.994
2025-10-22 03:03 | 83616.805 | 95754.727 | -45854.375 | 0.87 | 0.87324 | 28321.82 | 26973.162 | 26973.162 | 33716.453 | 32367.793 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 226.202 | 226.72 | 228.792 | 50.006
2025-10-22 03:04 | 75524.852 | 87662.773 | -44505.715 | 0.86 | 0.86154 | 25624.504 | 24275.846 | 24275.846 | 31019.137 | 29670.479 | 26973.162 | -16183.896 | -16183.896 | -12137.923 | 226.073 | 226.655 | 228.878 | 50.013
2025-10-22 03:05 | 76873.508 | 89011.43 | -45854.375 | 0.86 | 0.86364 | 26973.162 | 25624.504 | 24275.846 | 31019.137 | 31019.137 | 26973.162 | -16183.896 | -17532.555 | -12137.923 | 226.137 | 226.677 | 228.986 | 50.01
2025-10-22 03:06 | 76873.508 | 90360.094 | -45854.375 | 0.85 | 0.85075 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 31019.137 | 28321.82 | -16183.896 | -17532.555 | -12137.923 | 226.051 | 226.526 | 228.727 | 50.009
2025-10-22 03:07 | 82268.141 | 94406.063 | -44505.715 | 0.87 | 0.87143 | 28321.82 | 28321.82 | 26973.162 | 32367.793 | 32367.793 | 28321.82 | -16183.896 | -17532.555 | -12137.923 | 225.641 | 226.137 | 228.554 | 50.003
2025-10-22 03:08 | 83616.805 | 97103.383 | -45854.375 | 0.87 | 0.86111 | 28321.82 | 28321.82 | 26973.162 | 32367.793 | 33716.453 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 226.116 | 226.785 | 228.792 | 50.003
2025-10-22 03:09 | 78222.172 | 90360.094 | -45854.375 | 0.86 | 0.86567 | 26973.162 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.526 | 227.281 | 229.094 | 50.011
2025-10-22 03:10 | 76873.508 | 89011.43 | -44505.715 | 0.86 | 0.86364 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.806 | 227.518 | 229.482 | 50.007
2025-10-22 03:11 | 78222.172 | 89011.43 | -44505.715 | 0.87 | 0.87879 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.18 | 226.828 | 228.662 | 50.005
2025-10-22 03:12 | 75524.852 | 86314.117 | -41808.402 | 0.87 | 0.875 | 25624.504 | 24275.846 | 24275.846 | 31019.137 | 28321.82 | 26973.162 | -14835.239 | -14835.239 | -12137.923 | 226.655 | 227.087 | 228.899 | 50.003
2025-10-22 03:13 | 79570.828 | 90360.094 | -43157.059 | 0.87 | 0.8806 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 226.31 | 226.914 | 228.511 | 50.003
2025-10-22 03:14 | 76873.508 | 87662.773 | -43157.059 | 0.87 | 0.87692 | 26973.162 | 22927.188 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 225.986 | 226.828 | 228.166 | 49.999
2025-10-22 03:15 | 79570.828 | 91708.75 | -44505.715 | 0.87 | 0.86765 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 226.439 | 227.367 | 228.489 | 49.998
2025-10-22 03:16 | 80919.484 | 91708.75 | -44505.715 | 0.87 | 0.88235 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 226.418 | 227.669 | 228.382 | 49.995
2025-10-22 03:17 | 80919.484 | 93057.406 | -44505.715 | 0.87 | 0.86957 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 226.051 | 227.324 | 227.864 | 49.999
2025-10-22 03:18 | 78222.172 | 90360.094 | -43157.059 | 0.87 | 0.86567 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.526 | 227.734 | 228.252 | 49.996
2025-10-22 03:19 | 78222.172 | 90360.094 | -43157.059 | 0.87 | 0.86567 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.871 | 228.144 | 228.748 | 50.013
2025-10-22 03:20 | 78222.172 | 90360.094 | -43157.059 | 0.87 | 0.86567 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.18 | 227.432 | 228.576 | 50.011
2025-10-22 03:21 | 80919.484 | 93057.406 | -45854.375 | 0.87 | 0.86957 | 28321.82 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 226.137 | 227.432 | 228.597 | 50.006
2025-10-22 03:22 | 78222.172 | 90360.094 | -43157.059 | 0.87 | 0.86567 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 226.31 | 227.95 | 228.77 | 49.997
2025-10-22 03:23 | 75524.852 | 89011.43 | -44505.715 | 0.86 | 0.84848 | 26973.162 | 24275.846 | 24275.846 | 31019.137 | 29670.479 | 26973.162 | -16183.896 | -16183.896 | -12137.923 | 226.612 | 227.95 | 229.137 | 50.009
2025-10-22 03:24 | 71478.875 | 83616.805 | -43157.059 | 0.86 | 0.85484 | 25624.504 | 22927.188 | 22927.188 | 29670.479 | 28321.82 | 25624.504 | -14835.239 | -16183.896 | -12137.923 | 226.634 | 227.562 | 229.158 | 50.02
2025-10-22 03:25 | 70130.219 | 80919.484 | -39111.086 | 0.87 | 0.86667 | 24275.846 | 22927.188 | 22927.188 | 28321.82 | 26973.162 | 25624.504 | -13486.581 | -14835.239 | -10789.265 | 226.936 | 227.799 | 229.288 | 50.011
2025-10-22 03:26 | 74176.195 | 83616.805 | -37762.426 | 0.89 | 0.8871 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 226.72 | 227.518 | 228.835 | 50.017
2025-10-22 03:27 | 72827.539 | 82268.141 | -37762.426 | 0.88 | 0.88525 | 24275.846 | 24275.846 | 22927.188 | 28321.82 | 28321.82 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 226.483 | 227.13 | 228.899 | 50.019
2025-10-22 03:28 | 82268.141 | 93057.406 | -44505.715 | 0.87 | 0.88406 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.663 | 226.72 | 228.144 | 50.012
2025-10-22 03:29 | 78222.172 | 90360.094 | -44505.715 | 0.87 | 0.86567 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 225.706 | 226.936 | 228.166 | 50.011
2025-10-22 03:30 | 79570.828 | 91708.75 | -44505.715 | 0.87 | 0.86765 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.555 | 226.547 | 227.756 | 50.024
2025-10-22 03:31 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 225.878 | 226.612 | 227.885 | 50.02
2025-10-22 03:32 | 80919.484 | 93057.406 | -44505.715 | 0.87 | 0.86957 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.986 | 226.893 | 228.015 | 50.016
2025-10-22 03:33 | 79570.828 | 91708.75 | -44505.715 | 0.87 | 0.86765 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.18 | 226.871 | 228.079 | 50.02
2025-10-22 03:34 | 78222.172 | 90360.094 | -44505.715 | 0.86 | 0.86567 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 31019.137 | 28321.82 | -16183.896 | -17532.555 | -12137.923 | 226.483 | 227.173 | 228.576 | 50.024
2025-10-22 03:35 | 74176.195 | 86314.117 | -43157.059 | 0.86 | 0.85938 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 29670.479 | 26973.162 | -14835.239 | -16183.896 | -12137.923 | 226.029 | 226.569 | 228.187 | 50.027
2025-10-22 03:36 | 78222.172 | 87662.773 | -39111.086 | 0.89 | 0.89231 | 25624.504 | 26973.162 | 25624.504 | 29670.479 | 29670.479 | 28321.82 | -13486.581 | -14835.239 | -10789.265 | 226.116 | 226.439 | 228.123 | 50.027
2025-10-22 03:37 | 78222.172 | 87662.773 | -40459.742 | 0.89 | 0.89231 | 25624.504 | 26973.162 | 25624.504 | 29670.479 | 31019.137 | 28321.82 | -13486.581 | -14835.239 | -12137.923 | 226.094 | 226.461 | 228.058 | 50.023
2025-10-22 03:38 | 86314.117 | 98452.039 | -44505.715 | 0.89 | 0.87671 | 29670.479 | 28321.82 | 28321.82 | 33716.453 | 33716.453 | 31019.137 | -16183.896 | -16183.896 | -12137.923 | 225.943 | 226.418 | 228.015 | 50.025
2025-10-22 03:39 | 83616.805 | 95754.727 | -45854.375 | 0.87 | 0.87324 | 29670.479 | 26973.162 | 26973.162 | 33716.453 | 32367.793 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 225.77 | 226.353 | 227.777 | 50.023
2025-10-22 03:40 | 78222.172 | 90360.094 | -44505.715 | 0.87 | 0.86567 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.202 | 226.763 | 227.95 | 50.017
2025-10-22 03:41 | 72827.539 | 83616.805 | -40459.742 | 0.87 | 0.87097 | 25624.504 | 22927.188 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -12137.923 | 226.008 | 226.461 | 228.036 | 50.02
2025-10-22 03:42 | 72827.539 | 82268.141 | -36413.77 | 0.89 | 0.88525 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 225.727 | 225.965 | 227.95 | 50.02
2025-10-22 03:43 | 76873.508 | 86314.117 | -37762.426 | 0.89 | 0.89062 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 29670.479 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 225.792 | 225.9 | 228.058 | 50.009
2025-10-22 03:44 | 78222.172 | 86314.117 | -39111.086 | 0.89 | 0.90625 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 29670.479 | 28321.82 | -13486.581 | -13486.581 | -10789.265 | 225.727 | 226.353 | 228.403 | 50.002
2025-10-22 03:45 | 79570.828 | 87662.773 | -37762.426 | 0.9 | 0.90769 | 26973.162 | 26973.162 | 25624.504 | 29670.479 | 29670.479 | 28321.82 | -13486.581 | -13486.581 | -10789.265 | 226.224 | 226.893 | 228.77 | 50.014
2025-10-22 03:46 | 78222.172 | 87662.773 | -40459.742 | 0.88 | 0.89231 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 29670.479 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 226.677 | 227.324 | 229.115 | 50.017
2025-10-22 03:47 | 75524.852 | 84965.461 | -37762.426 | 0.89 | 0.88889 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 226.634 | 227.497 | 229.029 | 50.009
2025-10-22 03:48 | 80919.484 | 90360.094 | -40459.742 | 0.89 | 0.89552 | 26973.162 | 26973.162 | 26973.162 | 31019.137 | 31019.137 | 29670.479 | -14835.239 | -13486.581 | -12137.923 | 226.655 | 227.605 | 228.899 | 50.001
2025-10-22 03:49 | 75524.852 | 84965.461 | -39111.086 | 0.89 | 0.88889 | 25624.504 | 24275.846 | 25624.504 | 29670.479 | 26973.162 | 28321.82 | -13486.581 | -13486.581 | -10789.265 | 227.108 | 227.756 | 229.007 | 49.995
2025-10-22 03:50 | 75524.852 | 84965.461 | -37762.426 | 0.89 | 0.88889 | 25624.504 | 24275.846 | 25624.504 | 29670.479 | 26973.162 | 28321.82 | -13486.581 | -13486.581 | -10789.265 | 226.806 | 227.216 | 229.029 | 49.99
2025-10-22 03:51 | 75524.852 | 84965.461 | -37762.426 | 0.89 | 0.88889 | 26973.162 | 22927.188 | 25624.504 | 29670.479 | 26973.162 | 28321.82 | -14835.239 | -13486.581 | -10789.265 | 226.18 | 225.943 | 228.166 | 49.996
2025-10-22 03:52 | 74176.195 | 83616.805 | -37762.426 | 0.89 | 0.8871 | 25624.504 | 22927.188 | 25624.504 | 29670.479 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 226.526 | 226.871 | 228.748 | 49.999
2025-10-22 03:53 | 79570.828 | 90360.094 | -40459.742 | 0.89 | 0.8806 | 28321.82 | 25624.504 | 26973.162 | 31019.137 | 28321.82 | 29670.479 | -14835.239 | -13486.581 | -12137.923 | 226.094 | 226.59 | 228.425 | 50
2025-10-22 03:54 | 78222.172 | 87662.773 | -39111.086 | 0.89 | 0.89231 | 26973.162 | 25624.504 | 26973.162 | 31019.137 | 28321.82 | 29670.479 | -14835.239 | -13486.581 | -12137.923 | 225.965 | 226.483 | 228.144 | 50.008
2025-10-22 03:55 | 79570.828 | 89011.43 | -40459.742 | 0.89 | 0.89394 | 26973.162 | 25624.504 | 26973.162 | 31019.137 | 28321.82 | 29670.479 | -14835.239 | -13486.581 | -12137.923 | 225.598 | 226.267 | 227.842 | 50.012
2025-10-22 03:56 | 75524.852 | 84965.461 | -37762.426 | 0.89 | 0.88889 | 25624.504 | 24275.846 | 25624.504 | 29670.479 | 26973.162 | 28321.82 | -13486.581 | -12137.923 | -10789.265 | 226.051 | 226.785 | 228.252 | 50.009
2025-10-22 03:57 | 72827.539 | 82268.141 | -39111.086 | 0.88 | 0.88525 | 25624.504 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 226.547 | 227.216 | 228.662 | 50.015
2025-10-22 03:58 | 79570.828 | 90360.094 | -40459.742 | 0.89 | 0.8806 | 26973.162 | 26973.162 | 26973.162 | 31019.137 | 29670.479 | 29670.479 | -14835.239 | -14835.239 | -12137.923 | 226.18 | 226.677 | 228.619 | 50.02
2025-10-22 03:59 | 80919.484 | 90360.094 | -40459.742 | 0.89 | 0.89552 | 26973.162 | 26973.162 | 26973.162 | 31019.137 | 29670.479 | 29670.479 | -14835.239 | -13486.581 | -12137.923 | 225.684 | 226.073 | 228.144 | 50.025
2025-10-22 04:00 | 80919.484 | 90360.094 | -40459.742 | 0.89 | 0.89552 | 26973.162 | 26973.162 | 26973.162 | 31019.137 | 31019.137 | 28321.82 | -14835.239 | -14835.239 | -10789.265 | 225.274 | 225.274 | 227.648 | 50.016
2025-10-22 04:01 | 82268.141 | 93057.406 | -41808.402 | 0.89 | 0.88406 | 26973.162 | 29670.479 | 26973.162 | 31019.137 | 33716.453 | 29670.479 | -14835.239 | -16183.896 | -12137.923 | 225.447 | 225.36 | 227.885 | 50.025
2025-10-22 04:02 | 84965.461 | 95754.727 | -43157.059 | 0.89 | 0.88732 | 26973.162 | 29670.479 | 26973.162 | 31019.137 | 33716.453 | 29670.479 | -14835.239 | -16183.896 | -12137.923 | 225.576 | 225.641 | 227.972 | 50.019
2025-10-22 04:03 | 79570.828 | 90360.094 | -41808.402 | 0.88 | 0.8806 | 26973.162 | 28321.82 | 25624.504 | 29670.479 | 32367.793 | 28321.82 | -14835.239 | -16183.896 | -12137.923 | 225.037 | 225.253 | 227.367 | 50.016
2025-10-22 04:04 | 80919.484 | 91708.75 | -41808.402 | 0.89 | 0.88235 | 26973.162 | 26973.162 | 26973.162 | 31019.137 | 31019.137 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 224.886 | 224.994 | 226.914 | 50.015
2025-10-22 04:05 | 79570.828 | 89011.43 | -40459.742 | 0.89 | 0.89394 | 26973.162 | 26973.162 | 25624.504 | 29670.479 | 31019.137 | 28321.82 | -13486.581 | -14835.239 | -12137.923 | 224.778 | 225.317 | 227.022 | 50.002
2025-10-22 04:06 | 76873.508 | 87662.773 | -39111.086 | 0.89 | 0.87692 | 26973.162 | 25624.504 | 25624.504 | 29670.479 | 29670.479 | 28321.82 | -13486.581 | -13486.581 | -12137.923 | 225.274 | 225.965 | 227.475 | 50.003
2025-10-22 04:07 | 78222.172 | 87662.773 | -40459.742 | 0.89 | 0.89231 | 26973.162 | 24275.846 | 25624.504 | 29670.479 | 28321.82 | 28321.82 | -13486.581 | -13486.581 | -12137.923 | 225.425 | 226.137 | 227.583 | 50.003
2025-10-22 04:08 | 75524.852 | 86314.117 | -40459.742 | 0.88 | 0.875 | 25624.504 | 24275.846 | 25624.504 | 29670.479 | 28321.82 | 28321.82 | -14835.239 | -13486.581 | -12137.923 | 226.051 | 226.288 | 228.144 | 49.999
2025-10-22 04:09 | 78222.172 | 87662.773 | -40459.742 | 0.89 | 0.89231 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -14835.239 | -13486.581 | -12137.923 | 225.231 | 225.468 | 227.324 | 50.011
2025-10-22 04:10 | 76873.508 | 86314.117 | -39111.086 | 0.89 | 0.89062 | 26973.162 | 24275.846 | 25624.504 | 29670.479 | 28321.82 | 28321.82 | -13486.581 | -13486.581 | -12137.923 | 224.476 | 224.584 | 226.504 | 50.008
2025-10-22 04:11 | 75524.852 | 84965.461 | -39111.086 | 0.89 | 0.88889 | 25624.504 | 24275.846 | 25624.504 | 29670.479 | 26973.162 | 28321.82 | -13486.581 | -13486.581 | -12137.923 | 225.663 | 225.835 | 227.691 | 50.003
2025-10-22 04:12 | 75524.852 | 84965.461 | -39111.086 | 0.88 | 0.88889 | 25624.504 | 22927.188 | 25624.504 | 29670.479 | 26973.162 | 28321.82 | -14835.239 | -13486.581 | -12137.923 | 226.288 | 226.245 | 228.23 | 50.003
2025-10-22 04:13 | 74176.195 | 83616.805 | -37762.426 | 0.89 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 225.49 | 225.792 | 227.583 | 50.008
2025-10-22 04:14 | 72827.539 | 82268.141 | -40459.742 | 0.88 | 0.88525 | 25624.504 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -14835.239 | -13486.581 | -12137.923 | 226.029 | 226.245 | 227.993 | 50.007
2025-10-22 04:15 | 76873.508 | 87662.773 | -40459.742 | 0.89 | 0.87692 | 26973.162 | 24275.846 | 25624.504 | 29670.479 | 28321.82 | 28321.82 | -13486.581 | -13486.581 | -12137.923 | 225.922 | 226.461 | 227.928 | 50.007
2025-10-22 04:16 | 76873.508 | 86314.117 | -40459.742 | 0.88 | 0.89062 | 26973.162 | 24275.846 | 25624.504 | 29670.479 | 28321.82 | 28321.82 | -14835.239 | -13486.581 | -12137.923 | 225.749 | 226.18 | 227.518 | 50
2025-10-22 04:17 | 74176.195 | 84965.461 | -39111.086 | 0.88 | 0.87302 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 226.073 | 226.612 | 227.626 | 50.003
2025-10-22 04:18 | 75524.852 | 84965.461 | -37762.426 | 0.89 | 0.88889 | 26973.162 | 24275.846 | 25624.504 | 29670.479 | 28321.82 | 28321.82 | -13486.581 | -13486.581 | -12137.923 | 226.073 | 226.547 | 227.518 | 50.008
2025-10-22 04:19 | 76873.508 | 86314.117 | -39111.086 | 0.89 | 0.89062 | 26973.162 | 25624.504 | 25624.504 | 29670.479 | 28321.82 | 28321.82 | -13486.581 | -13486.581 | -12137.923 | 226.073 | 226.439 | 227.713 | 50.017
2025-10-22 04:20 | 75524.852 | 84965.461 | -39111.086 | 0.89 | 0.88889 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 226.008 | 226.439 | 227.907 | 50.019
2025-10-22 04:21 | 75524.852 | 84965.461 | -37762.426 | 0.89 | 0.88889 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 225.468 | 225.857 | 227.346 | 50.016
2025-10-22 04:22 | 74176.195 | 83616.805 | -37762.426 | 0.89 | 0.8871 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 225.663 | 226.202 | 227.885 | 50.009
2025-10-22 04:23 | 82268.141 | 91708.75 | -43157.059 | 0.88 | 0.89706 | 26973.162 | 26973.162 | 26973.162 | 31019.137 | 31019.137 | 29670.479 | -14835.239 | -14835.239 | -12137.923 | 225.663 | 226.202 | 228.036 | 50.011
2025-10-22 04:24 | 76873.508 | 86314.117 | -40459.742 | 0.88 | 0.89062 | 25624.504 | 25624.504 | 24275.846 | 29670.479 | 29670.479 | 26973.162 | -13486.581 | -14835.239 | -12137.923 | 226.094 | 226.72 | 228.36 | 50.02
2025-10-22 04:25 | 71478.875 | 80919.484 | -37762.426 | 0.88 | 0.88333 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 225.576 | 226.267 | 227.907 | 50.012
2025-10-22 04:26 | 70130.219 | 79570.828 | -37762.426 | 0.88 | 0.88136 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 25624.504 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 225.555 | 226.634 | 228.058 | 50.005
2025-10-22 04:27 | 74176.195 | 83616.805 | -39111.086 | 0.88 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 225.9 | 227.13 | 228.403 | 50.005
2025-10-22 04:28 | 74176.195 | 83616.805 | -39111.086 | 0.88 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 225.986 | 227.13 | 228.511 | 49.987
2025-10-22 04:29 | 71478.875 | 80919.484 | -37762.426 | 0.88 | 0.88333 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 225.9 | 226.936 | 228.554 | 49.977
2025-10-22 04:30 | 76873.508 | 86314.117 | -40459.742 | 0.88 | 0.89062 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 226.202 | 227.108 | 228.835 | 50
2025-10-22 04:31 | 78222.172 | 90360.094 | -45854.375 | 0.86 | 0.86567 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.396 | 227.065 | 229.007 | 49.993
2025-10-22 04:32 | 80919.484 | 94406.063 | -45854.375 | 0.87 | 0.85714 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 32367.793 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 225.706 | 226.59 | 228.36 | 50.009
2025-10-22 04:33 | 83616.805 | 94406.063 | -45854.375 | 0.87 | 0.88571 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 32367.793 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 226.267 | 227.238 | 228.533 | 50.022
2025-10-22 04:34 | 86314.117 | 98452.039 | -47203.031 | 0.87 | 0.87671 | 29670.479 | 28321.82 | 28321.82 | 33716.453 | 33716.453 | 31019.137 | -17532.555 | -17532.555 | -13486.581 | 225.792 | 226.806 | 228.166 | 50.013
2025-10-22 04:35 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.296 | 226.073 | 227.82 | 50.011
2025-10-22 04:36 | 82268.141 | 94406.063 | -44505.715 | 0.87 | 0.87143 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 32367.793 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.36 | 226.332 | 227.972 | 50.012
2025-10-22 04:37 | 82268.141 | 94406.063 | -44505.715 | 0.88 | 0.87143 | 28321.82 | 26973.162 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.584 | 225.188 | 227.238 | 50.02
2025-10-22 04:38 | 83616.805 | 95754.727 | -45854.375 | 0.87 | 0.87324 | 29670.479 | 26973.162 | 28321.82 | 33716.453 | 32367.793 | 31019.137 | -17532.555 | -16183.896 | -12137.923 | 224.799 | 225.231 | 227.475 | 50.009
2025-10-22 04:39 | 84965.461 | 95754.727 | -44505.715 | 0.88 | 0.88732 | 29670.479 | 26973.162 | 28321.82 | 33716.453 | 32367.793 | 31019.137 | -16183.896 | -16183.896 | -12137.923 | 224.648 | 225.447 | 227.713 | 50.031
2025-10-22 04:40 | 84965.461 | 97103.383 | -45854.375 | 0.88 | 0.875 | 29670.479 | 26973.162 | 28321.82 | 33716.453 | 32367.793 | 31019.137 | -16183.896 | -16183.896 | -12137.923 | 225.274 | 225.857 | 227.95 | 50.024
2025-10-22 04:41 | 82268.141 | 94406.063 | -44505.715 | 0.88 | 0.87143 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.907 | 225.835 | 227.518 | 50
2025-10-22 04:42 | 83616.805 | 94406.063 | -44505.715 | 0.88 | 0.88571 | 29670.479 | 26973.162 | 26973.162 | 33716.453 | 32367.793 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.54 | 225.684 | 227.303 | 50.005
2025-10-22 04:43 | 78222.172 | 89011.43 | -43157.059 | 0.87 | 0.87879 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -14835.239 | -16183.896 | -12137.923 | 224.929 | 226.18 | 227.303 | 50.001
2025-10-22 04:44 | 80919.484 | 93057.406 | -43157.059 | 0.88 | 0.86957 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.476 | 225.404 | 226.59 | 50.008
2025-10-22 04:45 | 82268.141 | 93057.406 | -43157.059 | 0.88 | 0.88406 | 29670.479 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.433 | 225.598 | 226.871 | 50.016
2025-10-22 04:46 | 82268.141 | 94406.063 | -44505.715 | 0.88 | 0.87143 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 224.756 | 225.986 | 227.324 | 50.023
2025-10-22 04:47 | 82268.141 | 94406.063 | -44505.715 | 0.87 | 0.87143 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.476 | 225.49 | 226.828 | 50.02
2025-10-22 04:48 | 83616.805 | 94406.063 | -44505.715 | 0.88 | 0.88571 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.584 | 225.468 | 226.677 | 50.019
2025-10-22 04:49 | 78222.172 | 89011.43 | -43157.059 | 0.87 | 0.87879 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 224.433 | 225.598 | 226.72 | 50.017
2025-10-22 04:50 | 78222.172 | 89011.43 | -41808.402 | 0.88 | 0.87879 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 224.648 | 225.706 | 226.957 | 50.017
2025-10-22 04:51 | 76873.508 | 89011.43 | -41808.402 | 0.87 | 0.86364 | 28321.82 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 224.994 | 226.051 | 227.281 | 50.015
2025-10-22 04:52 | 80919.484 | 91708.75 | -43157.059 | 0.88 | 0.88235 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.433 | 225.663 | 226.871 | 50.006
2025-10-22 04:53 | 79570.828 | 90360.094 | -44505.715 | 0.87 | 0.8806 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 224.605 | 225.835 | 226.849 | 50.006
2025-10-22 04:54 | 75524.852 | 87662.773 | -43157.059 | 0.86 | 0.86154 | 26973.162 | 22927.188 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 224.843 | 225.922 | 227.13 | 50.007
2025-10-22 04:55 | 70130.219 | 79570.828 | -37762.426 | 0.87 | 0.88136 | 25624.504 | 21578.529 | 22927.188 | 28321.82 | 25624.504 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 225.749 | 226.828 | 227.993 | 50.01
2025-10-22 04:56 | 74176.195 | 82268.141 | -36413.77 | 0.9 | 0.90164 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 25624.504 | -12137.923 | -13486.581 | -10789.265 | 224.756 | 225.576 | 226.957 | 49.988
2025-10-22 04:57 | 79570.828 | 89011.43 | -39111.086 | 0.89 | 0.89394 | 26973.162 | 26973.162 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -13486.581 | -14835.239 | -10789.265 | 224.174 | 225.209 | 226.439 | 49.991
2025-10-22 04:58 | 79570.828 | 90360.094 | -41808.402 | 0.88 | 0.8806 | 28321.82 | 25624.504 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -14835.239 | -14835.239 | -10789.265 | 226.547 | 227.583 | 229.007 | 49.998
2025-10-22 04:59 | 79570.828 | 90360.094 | -43157.059 | 0.87 | 0.8806 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -14835.239 | -16183.896 | -12137.923 | 227.087 | 227.993 | 229.547 | 50.008
2025-10-22 05:00 | 75524.852 | 87662.773 | -43157.059 | 0.87 | 0.86154 | 26973.162 | 24275.846 | 24275.846 | 31019.137 | 29670.479 | 26973.162 | -14835.239 | -16183.896 | -12137.923 | 227.691 | 228.209 | 230.453 | 50.004
2025-10-22 05:01 | 78222.172 | 90360.094 | -44505.715 | 0.86 | 0.86567 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 228.015 | 228.511 | 230.734 | 50.017
2025-10-22 05:02 | 82268.141 | 93057.406 | -44505.715 | 0.88 | 0.88406 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 227.065 | 227.41 | 229.741 | 50.015
2025-10-22 05:03 | 78222.172 | 89011.43 | -43157.059 | 0.87 | 0.87879 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -10789.265 | 227.799 | 227.885 | 230.194 | 50.026
2025-10-22 05:04 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 28321.82 | 26973.162 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 227.713 | 227.993 | 230.108 | 50.025
2025-10-22 05:05 | 83616.805 | 95754.727 | -45854.375 | 0.87 | 0.87324 | 29670.479 | 26973.162 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 227.583 | 227.691 | 229.719 | 50.013
2025-10-22 05:06 | 76873.508 | 87662.773 | -43157.059 | 0.87 | 0.87692 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 29670.479 | 26973.162 | -16183.896 | -16183.896 | -10789.265 | 228.144 | 228.36 | 230.151 | 50.016
2025-10-22 05:07 | 82268.141 | 94406.063 | -44505.715 | 0.88 | 0.87143 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 32367.793 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 227.022 | 227.842 | 229.396 | 50.023
2025-10-22 05:08 | 80919.484 | 93057.406 | -44505.715 | 0.87 | 0.86957 | 28321.82 | 25624.504 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 226.634 | 227.346 | 229.202 | 50.008
2025-10-22 05:09 | 78222.172 | 89011.43 | -41808.402 | 0.87 | 0.87879 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 228.058 | 228.792 | 230.453 | 50.019
2025-10-22 05:10 | 80919.484 | 91708.75 | -43157.059 | 0.88 | 0.88235 | 28321.82 | 24275.846 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 227.281 | 228.079 | 229.655 | 50.017
2025-10-22 05:11 | 74176.195 | 86314.117 | -41808.402 | 0.87 | 0.85938 | 26973.162 | 22927.188 | 25624.504 | 31019.137 | 26973.162 | 26973.162 | -16183.896 | -14835.239 | -10789.265 | 227.734 | 228.489 | 230.043 | 50.005
2025-10-22 05:12 | 78222.172 | 89011.43 | -41808.402 | 0.88 | 0.87879 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -10789.265 | 227.065 | 227.993 | 229.59 | 50.008
2025-10-22 05:13 | 82268.141 | 93057.406 | -44505.715 | 0.88 | 0.88406 | 28321.82 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 227.54 | 228.295 | 230 | 49.997
2025-10-22 05:14 | 78222.172 | 89011.43 | -41808.402 | 0.87 | 0.87879 | 26973.162 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -10789.265 | 227.95 | 228.317 | 230.086 | 50.014
2025-10-22 05:15 | 71478.875 | 82268.141 | -40459.742 | 0.87 | 0.86885 | 25624.504 | 22927.188 | 22927.188 | 29670.479 | 26973.162 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 227.648 | 228.274 | 229.914 | 50.022
2025-10-22 05:16 | 70130.219 | 80919.484 | -40459.742 | 0.86 | 0.86667 | 24275.846 | 21578.529 | 22927.188 | 28321.82 | 26973.162 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 227.669 | 228.295 | 230.129 | 50.03
2025-10-22 05:17 | 67432.906 | 79570.828 | -40459.742 | 0.85 | 0.84746 | 24275.846 | 21578.529 | 21578.529 | 28321.82 | 26973.162 | 24275.846 | -14835.239 | -14835.239 | -10789.265 | 227.799 | 228.446 | 230.259 | 50.045
2025-10-22 05:18 | 68781.563 | 78222.172 | -36413.77 | 0.88 | 0.87931 | 22927.188 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 24275.846 | -13486.581 | -13486.581 | -9440.606 | 227.303 | 227.95 | 229.633 | 50.034
2025-10-22 05:19 | 66084.242 | 74176.195 | -35065.109 | 0.88 | 0.89091 | 22927.188 | 21578.529 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 227.864 | 228.792 | 230.065 | 50.028
2025-10-22 05:20 | 63386.93 | 72827.539 | -33716.453 | 0.88 | 0.87037 | 21578.529 | 20229.871 | 21578.529 | 25624.504 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 228.015 | 229.007 | 230.194 | 50.018
2025-10-22 05:21 | 67432.906 | 76873.508 | -36413.77 | 0.88 | 0.87719 | 22927.188 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 228.058 | 229.18 | 230.345 | 50.02
2025-10-22 05:22 | 62038.273 | 71478.875 | -33716.453 | 0.88 | 0.86792 | 21578.529 | 20229.871 | 21578.529 | 25624.504 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 228.36 | 229.094 | 230.237 | 50.009
2025-10-22 05:23 | 63386.93 | 71478.875 | -33716.453 | 0.88 | 0.88679 | 21578.529 | 20229.871 | 21578.529 | 25624.504 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 227.216 | 228.015 | 229.18 | 49.998
2025-10-22 05:24 | 67432.906 | 75524.852 | -36413.77 | 0.88 | 0.89286 | 22927.188 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 24275.846 | -13486.581 | -12137.923 | -10789.265 | 227.216 | 227.626 | 229.029 | 49.988
2025-10-22 05:25 | 67432.906 | 76873.508 | -35065.109 | 0.88 | 0.87719 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 24275.846 | -13486.581 | -12137.923 | -10789.265 | 227.259 | 227.562 | 228.964 | 49.986
2025-10-22 05:26 | 68781.563 | 76873.508 | -36413.77 | 0.88 | 0.89474 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 226.957 | 227.928 | 229.029 | 49.99
2025-10-22 05:27 | 64735.586 | 72827.539 | -35065.109 | 0.88 | 0.88889 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 226.914 | 227.626 | 228.899 | 50.008
2025-10-22 05:28 | 59340.957 | 68781.563 | -33716.453 | 0.87 | 0.86275 | 20229.871 | 18881.213 | 20229.871 | 24275.846 | 21578.529 | 21578.529 | -12137.923 | -12137.923 | -9440.606 | 227.669 | 228.187 | 229.59 | 50.005
2025-10-22 05:29 | 60689.613 | 70130.219 | -33716.453 | 0.87 | 0.86538 | 21578.529 | 18881.213 | 20229.871 | 24275.846 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 227.216 | 227.864 | 229.288 | 50.009
2025-10-22 05:30 | 63386.93 | 71478.875 | -35065.109 | 0.87 | 0.88679 | 21578.529 | 20229.871 | 21578.529 | 25624.504 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 226.612 | 226.979 | 228.511 | 50.007
2025-10-22 05:31 | 64735.586 | 72827.539 | -33716.453 | 0.88 | 0.88889 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 24275.846 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 226.547 | 227.065 | 228.705 | 50.024
2025-10-22 05:32 | 66084.242 | 75524.852 | -35065.109 | 0.88 | 0.875 | 21578.529 | 22927.188 | 20229.871 | 24275.846 | 26973.162 | 22927.188 | -12137.923 | -13486.581 | -9440.606 | 226.612 | 226.504 | 228.986 | 50.03
2025-10-22 05:33 | 71478.875 | 80919.484 | -37762.426 | 0.88 | 0.88333 | 22927.188 | 25624.504 | 22927.188 | 26973.162 | 29670.479 | 24275.846 | -12137.923 | -14835.239 | -10789.265 | 226.612 | 226.677 | 229.007 | 50.032
2025-10-22 05:34 | 68781.563 | 76873.508 | -35065.109 | 0.89 | 0.89474 | 22927.188 | 24275.846 | 21578.529 | 25624.504 | 28321.82 | 22927.188 | -12137.923 | -13486.581 | -9440.606 | 226.483 | 226.763 | 228.489 | 50.028
2025-10-22 05:35 | 68781.563 | 76873.508 | -35065.109 | 0.89 | 0.89474 | 22927.188 | 24275.846 | 21578.529 | 25624.504 | 28321.82 | 24275.846 | -12137.923 | -13486.581 | -9440.606 | 226.698 | 226.785 | 228.619 | 50.024
2025-10-22 05:36 | 66084.242 | 74176.195 | -35065.109 | 0.88 | 0.89091 | 21578.529 | 22927.188 | 20229.871 | 24275.846 | 26973.162 | 22927.188 | -12137.923 | -13486.581 | -9440.606 | 226.957 | 227.108 | 228.986 | 50.022
2025-10-22 05:37 | 66084.242 | 74176.195 | -33716.453 | 0.89 | 0.89091 | 21578.529 | 22927.188 | 21578.529 | 24275.846 | 26973.162 | 22927.188 | -12137.923 | -12137.923 | -8091.948 | 226.655 | 226.418 | 228.835 | 50.012
2025-10-22 05:38 | 67432.906 | 75524.852 | -33716.453 | 0.89 | 0.89286 | 22927.188 | 21578.529 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 226.936 | 227 | 228.835 | 50.015
2025-10-22 05:39 | 66084.242 | 74176.195 | -33716.453 | 0.89 | 0.89091 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 227.065 | 227.367 | 229.029 | 50.021
2025-10-22 05:40 | 60689.613 | 67432.906 | -32367.793 | 0.88 | 0.9 | 20229.871 | 18881.213 | 20229.871 | 24275.846 | 21578.529 | 22927.188 | -12137.923 | -10789.265 | -9440.606 | 227.065 | 227.691 | 229.245 | 50.014
2025-10-22 05:41 | 60689.613 | 68781.563 | -31019.137 | 0.89 | 0.88235 | 21578.529 | 18881.213 | 20229.871 | 24275.846 | 21578.529 | 22927.188 | -10789.265 | -10789.265 | -9440.606 | 226.655 | 227.259 | 228.813 | 50.005
2025-10-22 05:42 | 64735.586 | 72827.539 | -32367.793 | 0.89 | 0.88889 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 22927.188 | 24275.846 | -12137.923 | -10789.265 | -9440.606 | 227.108 | 227.41 | 229.051 | 50.02
2025-10-22 05:43 | 57992.297 | 66084.242 | -29670.479 | 0.89 | 0.87755 | 20229.871 | 17532.555 | 20229.871 | 22927.188 | 20229.871 | 21578.529 | -10789.265 | -10789.265 | -8091.948 | 227.648 | 227.756 | 229.007 | 50.006
2025-10-22 05:44 | 47203.031 | 55294.98 | -26973.162 | 0.87 | 0.85366 | 17532.555 | 14835.239 | 16183.896 | 20229.871 | 17532.555 | 17532.555 | -9440.606 | -9440.606 | -6743.291 | 228.036 | 228.425 | 229.331 | 50.004
2025-10-22 05:45 | 47203.031 | 55294.98 | -26973.162 | 0.87 | 0.85366 | 17532.555 | 14835.239 | 16183.896 | 20229.871 | 17532.555 | 17532.555 | -10789.265 | -9440.606 | -6743.291 | 227.842 | 228.123 | 229.072 | 50.021
2025-10-22 05:46 | 48551.691 | 56643.641 | -26973.162 | 0.87 | 0.85714 | 17532.555 | 14835.239 | 16183.896 | 20229.871 | 17532.555 | 18881.213 | -10789.265 | -9440.606 | -8091.948 | 226.828 | 227.583 | 228.252 | 50.031
2025-10-22 05:47 | 47203.031 | 52597.664 | -22927.188 | 0.9 | 0.89744 | 16183.896 | 16183.896 | 16183.896 | 17532.555 | 17532.555 | 17532.555 | -8091.948 | -6743.291 | -6743.291 | 226.806 | 227.734 | 228.101 | 50.022
2025-10-22 05:48 | 47203.031 | 52597.664 | -22927.188 | 0.9 | 0.89744 | 16183.896 | 16183.896 | 16183.896 | 17532.555 | 17532.555 | 17532.555 | -8091.948 | -6743.291 | -6743.291 | 227.669 | 228.425 | 228.77 | 50.019
2025-10-22 05:49 | 47203.031 | 51249.008 | -21578.529 | 0.9 | 0.92105 | 14835.239 | 14835.239 | 16183.896 | 17532.555 | 17532.555 | 17532.555 | -8091.948 | -6743.291 | -6743.291 | 229.115 | 229.957 | 230.194 | 50.017
2025-10-22 05:50 | 47203.031 | 52597.664 | -22927.188 | 0.9 | 0.89744 | 16183.896 | 14835.239 | 16183.896 | 17532.555 | 17532.555 | 17532.555 | -8091.948 | -8091.948 | -6743.291 | 229.914 | 230.108 | 230.561 | 50.019
2025-10-22 05:51 | 48551.691 | 55294.98 | -24275.846 | 0.9 | 0.87805 | 16183.896 | 17532.555 | 16183.896 | 17532.555 | 18881.213 | 17532.555 | -8091.948 | -8091.948 | -8091.948 | 229.978 | 230.173 | 230.669 | 50.019
2025-10-22 05:52 | 51249.008 | 56643.641 | -25624.504 | 0.89 | 0.90476 | 16183.896 | 17532.555 | 16183.896 | 18881.213 | 20229.871 | 18881.213 | -9440.606 | -9440.606 | -8091.948 | 230.151 | 230.324 | 231.252 | 50.005
2025-10-22 05:53 | 49900.348 | 55294.98 | -24275.846 | 0.89 | 0.90244 | 16183.896 | 17532.555 | 16183.896 | 17532.555 | 18881.213 | 17532.555 | -8091.948 | -8091.948 | -8091.948 | 230.065 | 230.453 | 231.252 | 49.992
2025-10-22 05:54 | 52597.664 | 57992.297 | -25624.504 | 0.89 | 0.90698 | 16183.896 | 18881.213 | 17532.555 | 18881.213 | 20229.871 | 18881.213 | -9440.606 | -9440.606 | -8091.948 | 228.835 | 229.051 | 230 | 49.992
2025-10-22 05:55 | 49900.348 | 55294.98 | -24275.846 | 0.89 | 0.90244 | 16183.896 | 17532.555 | 16183.896 | 17532.555 | 18881.213 | 17532.555 | -8091.948 | -8091.948 | -8091.948 | 230.043 | 230.237 | 231.208 | 50
2025-10-22 05:56 | 49900.348 | 55294.98 | -24275.846 | 0.9 | 0.90244 | 16183.896 | 17532.555 | 16183.896 | 17532.555 | 18881.213 | 17532.555 | -8091.948 | -8091.948 | -8091.948 | 229.784 | 230.043 | 231.165 | 49.997
2025-10-22 05:57 | 49900.348 | 56643.641 | -25624.504 | 0.89 | 0.88095 | 16183.896 | 17532.555 | 16183.896 | 17532.555 | 20229.871 | 18881.213 | -8091.948 | -8091.948 | -8091.948 | 229.935 | 230.561 | 231.338 | 50.016
2025-10-22 05:58 | 48551.691 | 53946.324 | -24275.846 | 0.89 | 0.9 | 14835.239 | 17532.555 | 14835.239 | 17532.555 | 20229.871 | 17532.555 | -8091.948 | -9440.606 | -8091.948 | 230.194 | 231.014 | 231.467 | 50.012
2025-10-22 05:59 | 48551.691 | 53946.324 | -24275.846 | 0.89 | 0.9 | 14835.239 | 17532.555 | 14835.239 | 17532.555 | 20229.871 | 17532.555 | -8091.948 | -9440.606 | -8091.948 | 230.324 | 230.842 | 231.467 | 50.024
2025-10-22 06:00 | 49900.348 | 56643.641 | -25624.504 | 0.89 | 0.88095 | 16183.896 | 18881.213 | 16183.896 | 17532.555 | 20229.871 | 17532.555 | -8091.948 | -9440.606 | -8091.948 | 229.827 | 230.259 | 230.949 | 50.033
2025-10-22 06:01 | 52597.664 | 59340.957 | -28321.82 | 0.88 | 0.88636 | 16183.896 | 18881.213 | 16183.896 | 18881.213 | 21578.529 | 18881.213 | -9440.606 | -10789.265 | -8091.948 | 230.432 | 230.712 | 231.446 | 50.036
2025-10-22 06:02 | 48551.691 | 55294.98 | -24275.846 | 0.89 | 0.87805 | 16183.896 | 17532.555 | 16183.896 | 17532.555 | 20229.871 | 17532.555 | -8091.948 | -9440.606 | -8091.948 | 230.475 | 230.388 | 231.381 | 50.049
2025-10-22 06:03 | 52597.664 | 59340.957 | -26973.162 | 0.89 | 0.88636 | 17532.555 | 17532.555 | 17532.555 | 18881.213 | 20229.871 | 18881.213 | -9440.606 | -9440.606 | -8091.948 | 230.194 | 230.324 | 231.122 | 50.018
2025-10-22 06:04 | 48551.691 | 53946.324 | -24275.846 | 0.9 | 0.9 | 16183.896 | 16183.896 | 16183.896 | 17532.555 | 17532.555 | 17532.555 | -8091.948 | -8091.948 | -8091.948 | 228.403 | 229.245 | 229.806 | 49.997
2025-10-22 06:05 | 47203.031 | 52597.664 | -22927.188 | 0.9 | 0.89744 | 16183.896 | 16183.896 | 16183.896 | 17532.555 | 17532.555 | 17532.555 | -8091.948 | -8091.948 | -6743.291 | 227.108 | 227.562 | 228.533 | 49.983
2025-10-22 06:06 | 49900.348 | 55294.98 | -24275.846 | 0.9 | 0.90244 | 16183.896 | 17532.555 | 16183.896 | 18881.213 | 18881.213 | 18881.213 | -8091.948 | -8091.948 | -8091.948 | 228.23 | 229.461 | 230.237 | 49.979
2025-10-22 06:07 | 52597.664 | 57992.297 | -24275.846 | 0.9 | 0.90698 | 17532.555 | 17532.555 | 17532.555 | 18881.213 | 20229.871 | 20229.871 | -8091.948 | -8091.948 | -8091.948 | 227.13 | 228.835 | 229.137 | 49.972
2025-10-22 06:08 | 47203.031 | 52597.664 | -22927.188 | 0.9 | 0.89744 | 14835.239 | 16183.896 | 16183.896 | 17532.555 | 17532.555 | 17532.555 | -8091.948 | -6743.291 | -8091.948 | 225.922 | 227.626 | 227.993 | 49.972
2025-10-22 06:09 | 47203.031 | 53946.324 | -24275.846 | 0.9 | 0.875 | 16183.896 | 16183.896 | 16183.896 | 17532.555 | 17532.555 | 17532.555 | -8091.948 | -8091.948 | -8091.948 | 227.972 | 229.266 | 230.065 | 49.973
2025-10-22 06:10 | 48551.691 | 55294.98 | -25624.504 | 0.88 | 0.87805 | 16183.896 | 16183.896 | 16183.896 | 18881.213 | 17532.555 | 17532.555 | -9440.606 | -9440.606 | -8091.948 | 227.13 | 227.885 | 229.029 | 49.964
2025-10-22 06:11 | 53946.324 | 60689.613 | -29670.479 | 0.87 | 0.88889 | 18881.213 | 16183.896 | 17532.555 | 21578.529 | 20229.871 | 20229.871 | -10789.265 | -10789.265 | -8091.948 | 227.605 | 228.446 | 229.741 | 49.966
2025-10-22 06:12 | 55294.98 | 63386.93 | -29670.479 | 0.88 | 0.87234 | 18881.213 | 17532.555 | 17532.555 | 21578.529 | 20229.871 | 20229.871 | -10789.265 | -10789.265 | -8091.948 | 226.936 | 227.907 | 229.094 | 49.963
2025-10-22 06:13 | 56643.641 | 64735.586 | -29670.479 | 0.88 | 0.875 | 18881.213 | 18881.213 | 18881.213 | 21578.529 | 21578.529 | 20229.871 | -10789.265 | -10789.265 | -8091.948 | 226.159 | 226.742 | 228.36 | 49.975
2025-10-22 06:14 | 60689.613 | 67432.906 | -29670.479 | 0.89 | 0.9 | 20229.871 | 20229.871 | 20229.871 | 24275.846 | 22927.188 | 21578.529 | -10789.265 | -10789.265 | -8091.948 | 225.727 | 225.576 | 227.864 | 49.974
2025-10-22 06:15 | 63386.93 | 71478.875 | -33716.453 | 0.88 | 0.88679 | 21578.529 | 21578.529 | 20229.871 | 24275.846 | 24275.846 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 225.49 | 226.267 | 227.972 | 49.984
2025-10-22 06:16 | 59340.957 | 67432.906 | -32367.793 | 0.88 | 0.88 | 20229.871 | 20229.871 | 18881.213 | 22927.188 | 22927.188 | 21578.529 | -10789.265 | -12137.923 | -9440.606 | 224.972 | 225.986 | 227.432 | 50.003
2025-10-22 06:17 | 67432.906 | 75524.852 | -33716.453 | 0.89 | 0.89286 | 22927.188 | 22927.188 | 21578.529 | 25624.504 | 25624.504 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 224.433 | 225.36 | 226.849 | 50.04
2025-10-22 06:18 | 70130.219 | 78222.172 | -35065.109 | 0.9 | 0.89655 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 224.389 | 225.49 | 226.763 | 50.043
2025-10-22 06:19 | 68781.563 | 76873.508 | -33716.453 | 0.89 | 0.89474 | 22927.188 | 22927.188 | 22927.188 | 25624.504 | 25624.504 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 223.483 | 224.605 | 226.008 | 50.037
2025-10-22 06:20 | 67432.906 | 75524.852 | -33716.453 | 0.89 | 0.89286 | 22927.188 | 21578.529 | 22927.188 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 223.85 | 225.037 | 226.159 | 50.032
2025-10-22 06:21 | 67432.906 | 75524.852 | -33716.453 | 0.89 | 0.89286 | 22927.188 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 223.872 | 225.015 | 226.137 | 50.002
2025-10-22 06:22 | 70130.219 | 79570.828 | -35065.109 | 0.9 | 0.88136 | 24275.846 | 22927.188 | 24275.846 | 26973.162 | 25624.504 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 223.677 | 224.886 | 226.051 | 50.01
2025-10-22 06:23 | 70130.219 | 78222.172 | -36413.77 | 0.89 | 0.89655 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 223.699 | 224.886 | 225.943 | 49.998
2025-10-22 06:24 | 66084.242 | 74176.195 | -33716.453 | 0.89 | 0.89091 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 224.411 | 225.533 | 227.152 | 49.994
2025-10-22 06:25 | 67432.906 | 76873.508 | -35065.109 | 0.89 | 0.87719 | 22927.188 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 223.31 | 224.886 | 226.353 | 49.989
2025-10-22 06:26 | 63386.93 | 71478.875 | -35065.109 | 0.88 | 0.88679 | 21578.529 | 20229.871 | 21578.529 | 25624.504 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -10789.265 | 223.591 | 225.274 | 226.763 | 49.993
2025-10-22 06:27 | 57992.297 | 66084.242 | -31019.137 | 0.88 | 0.87755 | 20229.871 | 17532.555 | 18881.213 | 22927.188 | 21578.529 | 21578.529 | -10789.265 | -10789.265 | -9440.606 | 224.433 | 225.986 | 227.324 | 50.001
2025-10-22 06:28 | 59340.957 | 67432.906 | -32367.793 | 0.87 | 0.88 | 20229.871 | 18881.213 | 20229.871 | 22927.188 | 21578.529 | 21578.529 | -12137.923 | -10789.265 | -9440.606 | 224.238 | 225.598 | 227.087 | 49.995
2025-10-22 06:29 | 62038.273 | 70130.219 | -32367.793 | 0.89 | 0.88462 | 20229.871 | 22927.188 | 20229.871 | 22927.188 | 25624.504 | 22927.188 | -10789.265 | -10789.265 | -10789.265 | 223.44 | 224.864 | 226.59 | 49.991
2025-10-22 06:30 | 60689.613 | 67432.906 | -29670.479 | 0.89 | 0.9 | 18881.213 | 21578.529 | 20229.871 | 21578.529 | 24275.846 | 21578.529 | -9440.606 | -10789.265 | -9440.606 | 223.634 | 224.756 | 226.461 | 50.009
2025-10-22 06:31 | 64735.586 | 72827.539 | -32367.793 | 0.89 | 0.88889 | 20229.871 | 22927.188 | 21578.529 | 22927.188 | 25624.504 | 24275.846 | -10789.265 | -10789.265 | -10789.265 | 222.987 | 224.152 | 226.073 | 50.025
2025-10-22 06:32 | 66084.242 | 74176.195 | -32367.793 | 0.9 | 0.89091 | 20229.871 | 24275.846 | 21578.529 | 22927.188 | 25624.504 | 24275.846 | -10789.265 | -10789.265 | -10789.265 | 223.505 | 225.015 | 226.461 | 50.031
2025-10-22 06:33 | 63386.93 | 70130.219 | -29670.479 | 0.9 | 0.90385 | 20229.871 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 22927.188 | -9440.606 | -10789.265 | -9440.606 | 223.095 | 224.692 | 225.835 | 50.012
2025-10-22 06:34 | 67432.906 | 75524.852 | -31019.137 | 0.9 | 0.89286 | 20229.871 | 25624.504 | 21578.529 | 22927.188 | 28321.82 | 24275.846 | -10789.265 | -10789.265 | -9440.606 | 222.728 | 223.958 | 225.663 | 50.008
2025-10-22 06:35 | 67432.906 | 75524.852 | -32367.793 | 0.9 | 0.89286 | 21578.529 | 25624.504 | 21578.529 | 22927.188 | 28321.82 | 24275.846 | -10789.265 | -12137.923 | -9440.606 | 222.318 | 222.879 | 224.713 | 50.004
2025-10-22 06:36 | 66084.242 | 72827.539 | -31019.137 | 0.91 | 0.90741 | 21578.529 | 22927.188 | 21578.529 | 24275.846 | 25624.504 | 24275.846 | -10789.265 | -10789.265 | -9440.606 | 222.771 | 222.987 | 224.821 | 50.004
2025-10-22 06:37 | 68781.563 | 75524.852 | -32367.793 | 0.91 | 0.91071 | 21578.529 | 24275.846 | 22927.188 | 24275.846 | 26973.162 | 24275.846 | -10789.265 | -10789.265 | -10789.265 | 221.886 | 222.555 | 224.087 | 49.987
2025-10-22 06:38 | 71478.875 | 80919.484 | -36413.77 | 0.89 | 0.88333 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -12137.923 | -13486.581 | -10789.265 | 224.864 | 225.878 | 226.957 | 50.001
2025-10-22 06:39 | 74176.195 | 82268.141 | -36413.77 | 0.89 | 0.90164 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -12137.923 | -10789.265 | 224.713 | 226.051 | 226.914 | 49.994
2025-10-22 06:40 | 71478.875 | 80919.484 | -36413.77 | 0.89 | 0.88333 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 25624.504 | 26973.162 | -12137.923 | -12137.923 | -10789.265 | 222.965 | 224.26 | 225.404 | 49.972
2025-10-22 06:41 | 71478.875 | 80919.484 | -36413.77 | 0.89 | 0.88333 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -12137.923 | -10789.265 | 224.389 | 225.878 | 227.108 | 49.975
2025-10-22 06:42 | 68781.563 | 78222.172 | -36413.77 | 0.89 | 0.87931 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 224.735 | 226.396 | 227.54 | 49.977
2025-10-22 06:43 | 68781.563 | 76873.508 | -35065.109 | 0.89 | 0.89474 | 22927.188 | 21578.529 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 224.368 | 225.835 | 227 | 49.986
2025-10-22 06:44 | 71478.875 | 80919.484 | -36413.77 | 0.89 | 0.88333 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 224.303 | 225.619 | 226.936 | 49.996
2025-10-22 06:45 | 72827.539 | 80919.484 | -35065.109 | 0.9 | 0.9 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -12137.923 | -12137.923 | -10789.265 | 223.548 | 224.929 | 226.634 | 50.002
2025-10-22 06:46 | 64735.586 | 72827.539 | -33716.453 | 0.89 | 0.88889 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 22927.188 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 224.152 | 225.166 | 226.698 | 50.028
2025-10-22 06:47 | 60689.613 | 68781.563 | -32367.793 | 0.88 | 0.88235 | 21578.529 | 18881.213 | 20229.871 | 24275.846 | 21578.529 | 22927.188 | -12137.923 | -10789.265 | -9440.606 | 224.368 | 225.641 | 226.742 | 50.041
2025-10-22 06:48 | 59340.957 | 67432.906 | -32367.793 | 0.88 | 0.88 | 20229.871 | 18881.213 | 20229.871 | 24275.846 | 21578.529 | 21578.529 | -12137.923 | -10789.265 | -9440.606 | 224.821 | 226.202 | 227.173 | 50.037
2025-10-22 06:49 | 57992.297 | 66084.242 | -31019.137 | 0.88 | 0.87755 | 20229.871 | 18881.213 | 18881.213 | 22927.188 | 21578.529 | 21578.529 | -10789.265 | -10789.265 | -9440.606 | 225.145 | 226.547 | 227.475 | 50.033
2025-10-22 06:50 | 57992.297 | 64735.586 | -28321.82 | 0.9 | 0.89583 | 18881.213 | 20229.871 | 18881.213 | 21578.529 | 21578.529 | 21578.529 | -9440.606 | -9440.606 | -9440.606 | 224.929 | 225.9 | 227.173 | 50.019
2025-10-22 06:51 | 57992.297 | 63386.93 | -28321.82 | 0.9 | 0.91489 | 18881.213 | 20229.871 | 18881.213 | 20229.871 | 22927.188 | 20229.871 | -9440.606 | -9440.606 | -9440.606 | 225.037 | 225.641 | 227.13 | 50.01
2025-10-22 06:52 | 60689.613 | 68781.563 | -31019.137 | 0.89 | 0.88235 | 18881.213 | 21578.529 | 20229.871 | 21578.529 | 24275.846 | 22927.188 | -10789.265 | -10789.265 | -9440.606 | 225.425 | 226.353 | 227.691 | 49.995
2025-10-22 06:53 | 57992.297 | 66084.242 | -29670.479 | 0.89 | 0.87755 | 18881.213 | 20229.871 | 18881.213 | 21578.529 | 22927.188 | 21578.529 | -9440.606 | -9440.606 | -9440.606 | 225.727 | 226.526 | 227.842 | 50.007
2025-10-22 06:54 | 56643.641 | 63386.93 | -28321.82 | 0.9 | 0.89362 | 17532.555 | 20229.871 | 18881.213 | 20229.871 | 22927.188 | 20229.871 | -9440.606 | -9440.606 | -9440.606 | 225.857 | 226.849 | 227.993 | 50.004
2025-10-22 06:55 | 59340.957 | 64735.586 | -28321.82 | 0.9 | 0.91667 | 18881.213 | 20229.871 | 18881.213 | 21578.529 | 22927.188 | 21578.529 | -9440.606 | -9440.606 | -9440.606 | 225.922 | 226.785 | 228.166 | 49.993
2025-10-22 06:56 | 59340.957 | 66084.242 | -28321.82 | 0.9 | 0.89796 | 18881.213 | 21578.529 | 18881.213 | 21578.529 | 22927.188 | 21578.529 | -9440.606 | -9440.606 | -9440.606 | 225.663 | 226.742 | 227.907 | 49.982
2025-10-22 06:57 | 57992.297 | 63386.93 | -25624.504 | 0.91 | 0.91489 | 18881.213 | 20229.871 | 18881.213 | 20229.871 | 22927.188 | 20229.871 | -8091.948 | -9440.606 | -8091.948 | 224.648 | 225.9 | 227.044 | 49.975
2025-10-22 06:58 | 62038.273 | 70130.219 | -33716.453 | 0.88 | 0.88462 | 21578.529 | 20229.871 | 20229.871 | 24275.846 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 226.029 | 227.303 | 228.662 | 49.982
2025-10-22 06:59 | 63386.93 | 71478.875 | -33716.453 | 0.88 | 0.88679 | 21578.529 | 20229.871 | 21578.529 | 25624.504 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 226.375 | 227.432 | 229.223 | 49.989
2025-10-22 07:00 | 66084.242 | 74176.195 | -33716.453 | 0.89 | 0.89091 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 224.929 | 225.965 | 227.669 | 50.003
2025-10-22 07:01 | 66084.242 | 75524.852 | -35065.109 | 0.88 | 0.875 | 22927.188 | 21578.529 | 22927.188 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 226.957 | 228.079 | 229.892 | 50.027
2025-10-22 07:02 | 67432.906 | 76873.508 | -36413.77 | 0.88 | 0.87719 | 22927.188 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 228.964 | 230 | 232.05 | 50.004
2025-10-22 07:03 | 74176.195 | 83616.805 | -39111.086 | 0.88 | 0.8871 | 24275.846 | 25624.504 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -14835.239 | -10789.265 | 229.461 | 230.065 | 232.395 | 50.01
2025-10-22 07:04 | 71478.875 | 80919.484 | -37762.426 | 0.88 | 0.88333 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 28321.82 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 229.029 | 229.719 | 231.532 | 50.002
2025-10-22 07:05 | 68781.563 | 78222.172 | -37762.426 | 0.87 | 0.87931 | 22927.188 | 22927.188 | 22927.188 | 26973.162 | 26973.162 | 24275.846 | -13486.581 | -13486.581 | -10789.265 | 229.461 | 230.669 | 232.18 | 49.997
2025-10-22 07:06 | 75524.852 | 84965.461 | -40459.742 | 0.88 | 0.88889 | 24275.846 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -13486.581 | -14835.239 | -12137.923 | 230.194 | 231.489 | 232.892 | 49.981
2025-10-22 07:07 | 74176.195 | 83616.805 | -39111.086 | 0.88 | 0.8871 | 24275.846 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 226.159 | 227.497 | 228.899 | 49.969
2025-10-22 07:08 | 70130.219 | 78222.172 | -33716.453 | 0.9 | 0.89655 | 22927.188 | 24275.846 | 22927.188 | 25624.504 | 26973.162 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 222.404 | 223.354 | 225.209 | 49.963
2025-10-22 07:09 | 64735.586 | 71478.875 | -31019.137 | 0.9 | 0.90566 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 22927.188 | 22927.188 | -10789.265 | -10789.265 | -8091.948 | 221.26 | 222.188 | 223.699 | 49.968
2025-10-22 07:10 | 62038.273 | 68781.563 | -29670.479 | 0.9 | 0.90196 | 21578.529 | 18881.213 | 20229.871 | 24275.846 | 21578.529 | 22927.188 | -10789.265 | -10789.265 | -8091.948 | 219.901 | 220.872 | 222.49 | 49.965
2025-10-22 07:11 | 71478.875 | 78222.172 | -33716.453 | 0.9 | 0.91379 | 24275.846 | 22927.188 | 24275.846 | 26973.162 | 25624.504 | 25624.504 | -12137.923 | -12137.923 | -9440.606 | 220.44 | 221.541 | 223.138 | 49.978
2025-10-22 07:12 | 64735.586 | 72827.539 | -32367.793 | 0.89 | 0.88889 | 21578.529 | 20229.871 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -10789.265 | -9440.606 | 220.311 | 221.347 | 223.116 | 49.989
2025-10-22 07:13 | 64735.586 | 72827.539 | -33716.453 | 0.89 | 0.88889 | 21578.529 | 21578.529 | 21578.529 | 25624.504 | 24275.846 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 219.707 | 220.548 | 222.728 | 49.986
2025-10-22 07:14 | 72827.539 | 80919.484 | -35065.109 | 0.9 | 0.9 | 24275.846 | 24275.846 | 24275.846 | 26973.162 | 26973.162 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 221.843 | 222.771 | 225.08 | 50.003
2025-10-22 07:15 | 72827.539 | 82268.141 | -36413.77 | 0.89 | 0.88525 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -12137.923 | -10789.265 | 223.246 | 224.54 | 226.504 | 49.976
2025-10-22 07:16 | 74176.195 | 82268.141 | -36413.77 | 0.9 | 0.90164 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -12137.923 | -10789.265 | 223.008 | 224.454 | 226.029 | 49.995
2025-10-22 07:17 | 70130.219 | 78222.172 | -35065.109 | 0.89 | 0.89655 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 223.44 | 224.929 | 226.31 | 50.013
2025-10-22 07:18 | 70130.219 | 78222.172 | -35065.109 | 0.89 | 0.89655 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 223.138 | 224.325 | 225.684 | 50.019
2025-10-22 07:19 | 67432.906 | 75524.852 | -33716.453 | 0.89 | 0.89286 | 22927.188 | 21578.529 | 22927.188 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 221.325 | 222.922 | 224.13 | 50.025
2025-10-22 07:20 | 70130.219 | 79570.828 | -35065.109 | 0.89 | 0.88136 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 223.267 | 224.972 | 226.202 | 50.01
2025-10-22 07:21 | 64735.586 | 72827.539 | -33716.453 | 0.89 | 0.88889 | 22927.188 | 21578.529 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 225.792 | 227.216 | 228.36 | 50.002
2025-10-22 07:22 | 64735.586 | 72827.539 | -32367.793 | 0.89 | 0.88889 | 21578.529 | 20229.871 | 21578.529 | 25624.504 | 22927.188 | 24275.846 | -12137.923 | -10789.265 | -9440.606 | 225.468 | 227.065 | 228.274 | 50.011
2025-10-22 07:23 | 60689.613 | 68781.563 | -32367.793 | 0.88 | 0.88235 | 21578.529 | 20229.871 | 20229.871 | 24275.846 | 22927.188 | 22927.188 | -10789.265 | -10789.265 | -9440.606 | 225.188 | 226.893 | 228.058 | 50.007
2025-10-22 07:24 | 66084.242 | 74176.195 | -32367.793 | 0.89 | 0.89091 | 22927.188 | 21578.529 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -10789.265 | -9440.606 | 226.137 | 227.497 | 228.425 | 49.999
2025-10-22 07:25 | 68781.563 | 76873.508 | -35065.109 | 0.89 | 0.89474 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 226.288 | 227.605 | 228.554 | 49.995
2025-10-22 07:26 | 68781.563 | 76873.508 | -33716.453 | 0.89 | 0.89474 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 225.943 | 227.281 | 228.338 | 49.998
2025-10-22 07:27 | 70130.219 | 79570.828 | -36413.77 | 0.89 | 0.88136 | 24275.846 | 22927.188 | 22927.188 | 28321.82 | 25624.504 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 225.814 | 227.238 | 228.705 | 50.006
2025-10-22 07:28 | 64735.586 | 74176.195 | -35065.109 | 0.88 | 0.87273 | 21578.529 | 21578.529 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 226.763 | 227.972 | 229.633 | 50.004
2025-10-22 07:29 | 75524.852 | 83616.805 | -36413.77 | 0.9 | 0.90323 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -12137.923 | -13486.581 | -10789.265 | 225.274 | 226.504 | 228.554 | 50.014
2025-10-22 07:30 | 76873.508 | 86314.117 | -39111.086 | 0.89 | 0.89062 | 26973.162 | 25624.504 | 25624.504 | 29670.479 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 225.727 | 226.785 | 229.007 | 50.005
2025-10-22 07:31 | 79570.828 | 90360.094 | -41808.402 | 0.89 | 0.8806 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 28321.82 | -14835.239 | -14835.239 | -10789.265 | 225.684 | 226.332 | 228.77 | 50.019
2025-10-22 07:32 | 78222.172 | 89011.43 | -41808.402 | 0.88 | 0.87879 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -14835.239 | -14835.239 | -10789.265 | 225.339 | 226.612 | 228.792 | 50.033
2025-10-22 07:33 | 78222.172 | 89011.43 | -41808.402 | 0.87 | 0.87879 | 26973.162 | 26973.162 | 24275.846 | 31019.137 | 31019.137 | 26973.162 | -14835.239 | -16183.896 | -10789.265 | 225.792 | 226.849 | 229.266 | 50.04
2025-10-22 07:34 | 78222.172 | 90360.094 | -43157.059 | 0.87 | 0.86567 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 31019.137 | 26973.162 | -14835.239 | -16183.896 | -10789.265 | 225.727 | 226.849 | 228.878 | 50.024
2025-10-22 07:35 | 79570.828 | 90360.094 | -43157.059 | 0.87 | 0.8806 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -10789.265 | 225.9 | 226.742 | 228.727 | 50.026
2025-10-22 07:36 | 76873.508 | 89011.43 | -43157.059 | 0.87 | 0.86364 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 29670.479 | 26973.162 | -14835.239 | -16183.896 | -10789.265 | 225.922 | 226.483 | 228.468 | 50.023
2025-10-22 07:37 | 75524.852 | 86314.117 | -41808.402 | 0.87 | 0.875 | 26973.162 | 24275.846 | 24275.846 | 31019.137 | 29670.479 | 26973.162 | -14835.239 | -16183.896 | -10789.265 | 225.145 | 225.878 | 228.079 | 50.021
2025-10-22 07:38 | 76873.508 | 87662.773 | -40459.742 | 0.88 | 0.87692 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 29670.479 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 225.943 | 226.677 | 229.094 | 50.022
2025-10-22 07:39 | 78222.172 | 90360.094 | -44505.715 | 0.87 | 0.86567 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.641 | 227.044 | 228.964 | 50.007
2025-10-22 07:40 | 72827.539 | 83616.805 | -41808.402 | 0.86 | 0.87097 | 25624.504 | 22927.188 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -12137.923 | 225.339 | 227.152 | 228.619 | 50.015
2025-10-22 07:41 | 76873.508 | 87662.773 | -43157.059 | 0.87 | 0.87692 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 225.706 | 227.324 | 229.007 | 50.01
2025-10-22 07:42 | 74176.195 | 86314.117 | -43157.059 | 0.86 | 0.85938 | 26973.162 | 22927.188 | 24275.846 | 31019.137 | 28321.82 | 26973.162 | -16183.896 | -16183.896 | -12137.923 | 225.641 | 227.173 | 228.792 | 49.994
2025-10-22 07:43 | 76873.508 | 86314.117 | -40459.742 | 0.88 | 0.89062 | 26973.162 | 24275.846 | 25624.504 | 29670.479 | 28321.82 | 28321.82 | -13486.581 | -13486.581 | -12137.923 | 225.145 | 227.389 | 228.166 | 49.994
2025-10-22 07:44 | 78222.172 | 90360.094 | -44505.715 | 0.87 | 0.86567 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 225.253 | 227.497 | 228.079 | 50.01
2025-10-22 07:45 | 78222.172 | 90360.094 | -45854.375 | 0.86 | 0.86567 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 225.943 | 227.648 | 228.921 | 49.997
2025-10-22 07:46 | 76873.508 | 87662.773 | -41808.402 | 0.88 | 0.87692 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 225.857 | 227.346 | 228.641 | 49.998
2025-10-22 07:47 | 72827.539 | 82268.141 | -37762.426 | 0.88 | 0.88525 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 226.224 | 227.756 | 229.137 | 50.003
2025-10-22 07:48 | 74176.195 | 83616.805 | -39111.086 | 0.89 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 225.77 | 227.562 | 228.727 | 50.014
2025-10-22 07:49 | 74176.195 | 83616.805 | -39111.086 | 0.88 | 0.8871 | 25624.504 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 226.137 | 227.669 | 228.899 | 50.006
2025-10-22 07:50 | 76873.508 | 86314.117 | -41808.402 | 0.88 | 0.89062 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 226.31 | 227.518 | 229.072 | 50.016
2025-10-22 07:51 | 74176.195 | 83616.805 | -37762.426 | 0.89 | 0.8871 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 225.878 | 227.065 | 228.533 | 50.004
2025-10-22 07:52 | 75524.852 | 86314.117 | -40459.742 | 0.88 | 0.875 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 29670.479 | 28321.82 | -14835.239 | -13486.581 | -12137.923 | 225.943 | 226.763 | 228.403 | 50.015
2025-10-22 07:53 | 75524.852 | 84965.461 | -39111.086 | 0.89 | 0.88889 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 225.296 | 226.116 | 227.885 | 50.002
2025-10-22 07:54 | 75524.852 | 84965.461 | -39111.086 | 0.89 | 0.88889 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 225.274 | 226.159 | 228.209 | 49.999
2025-10-22 07:55 | 74176.195 | 83616.805 | -37762.426 | 0.89 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 225.49 | 226.612 | 228.403 | 50.012
2025-10-22 07:56 | 67432.906 | 78222.172 | -37762.426 | 0.87 | 0.86207 | 22927.188 | 21578.529 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -13486.581 | -13486.581 | -12137.923 | 226.029 | 227.475 | 228.77 | 50.002
2025-10-22 07:57 | 72827.539 | 82268.141 | -37762.426 | 0.89 | 0.88525 | 25624.504 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 225.447 | 226.806 | 228.511 | 50.01
2025-10-22 07:58 | 71478.875 | 80919.484 | -37762.426 | 0.89 | 0.88333 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 224.95 | 226.763 | 228.187 | 50.012
2025-10-22 07:59 | 75524.852 | 83616.805 | -37762.426 | 0.89 | 0.90323 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 223.764 | 225.123 | 227 | 50.017
2025-10-22 08:00 | 79570.828 | 89011.43 | -39111.086 | 0.89 | 0.89394 | 26973.162 | 26973.162 | 25624.504 | 29670.479 | 31019.137 | 28321.82 | -13486.581 | -14835.239 | -12137.923 | 223.979 | 224.799 | 227.259 | 50.018
2025-10-22 08:01 | 76873.508 | 87662.773 | -39111.086 | 0.89 | 0.87692 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 29670.479 | 28321.82 | -13486.581 | -13486.581 | -10789.265 | 223.375 | 224.044 | 226.461 | 50.017
2025-10-22 08:02 | 74176.195 | 83616.805 | -37762.426 | 0.89 | 0.8871 | 24275.846 | 25624.504 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 223.44 | 224.001 | 226.569 | 49.982
2025-10-22 08:03 | 78222.172 | 87662.773 | -40459.742 | 0.89 | 0.89231 | 25624.504 | 26973.162 | 25624.504 | 29670.479 | 29670.479 | 28321.82 | -13486.581 | -14835.239 | -10789.265 | 224.497 | 224.972 | 227.497 | 50
2025-10-22 08:04 | 79570.828 | 89011.43 | -40459.742 | 0.89 | 0.89394 | 26973.162 | 26973.162 | 25624.504 | 29670.479 | 31019.137 | 28321.82 | -13486.581 | -14835.239 | -12137.923 | 225.447 | 226.634 | 228.684 | 49.996
2025-10-22 08:05 | 78222.172 | 89011.43 | -41808.402 | 0.88 | 0.87879 | 25624.504 | 26973.162 | 25624.504 | 29670.479 | 31019.137 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 225.468 | 226.569 | 228.748 | 50.001
2025-10-22 08:06 | 79570.828 | 89011.43 | -41808.402 | 0.89 | 0.89394 | 26973.162 | 25624.504 | 26973.162 | 31019.137 | 29670.479 | 29670.479 | -14835.239 | -13486.581 | -12137.923 | 225.468 | 226.914 | 228.641 | 50.023
2025-10-22 08:07 | 72827.539 | 82268.141 | -37762.426 | 0.88 | 0.88525 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 225.231 | 226.698 | 228.317 | 50.02
2025-10-22 08:08 | 76873.508 | 86314.117 | -40459.742 | 0.88 | 0.89062 | 25624.504 | 24275.846 | 25624.504 | 29670.479 | 28321.82 | 28321.82 | -13486.581 | -13486.581 | -12137.923 | 224.972 | 226.439 | 228.252 | 50.001
2025-10-22 08:09 | 75524.852 | 84965.461 | -39111.086 | 0.89 | 0.88889 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 225.706 | 226.698 | 228.835 | 49.997
2025-10-22 08:10 | 78222.172 | 89011.43 | -40459.742 | 0.89 | 0.87879 | 26973.162 | 26973.162 | 25624.504 | 29670.479 | 29670.479 | 28321.82 | -14835.239 | -13486.581 | -12137.923 | 225.619 | 226.547 | 229.051 | 49.991
2025-10-22 08:11 | 76873.508 | 84965.461 | -37762.426 | 0.9 | 0.90476 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 225.123 | 226.116 | 228.641 | 49.993
2025-10-22 08:12 | 79570.828 | 90360.094 | -41808.402 | 0.88 | 0.8806 | 26973.162 | 26973.162 | 25624.504 | 31019.137 | 31019.137 | 28321.82 | -14835.239 | -14835.239 | -13486.581 | 225.533 | 227.065 | 229.029 | 50.001
2025-10-22 08:13 | 78222.172 | 87662.773 | -40459.742 | 0.89 | 0.89231 | 25624.504 | 26973.162 | 25624.504 | 29670.479 | 29670.479 | 28321.82 | -13486.581 | -14835.239 | -12137.923 | 226.051 | 227.497 | 229.396 | 49.986
2025-10-22 08:14 | 72827.539 | 80919.484 | -37762.426 | 0.88 | 0.9 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 226.073 | 227.648 | 229.309 | 50.009
2025-10-22 08:15 | 71478.875 | 80919.484 | -39111.086 | 0.88 | 0.88333 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 225.382 | 227 | 228.727 | 50.023
2025-10-22 08:16 | 74176.195 | 83616.805 | -39111.086 | 0.88 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 224.864 | 226.72 | 228.123 | 50.025
2025-10-22 08:17 | 72827.539 | 83616.805 | -39111.086 | 0.88 | 0.87097 | 25624.504 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 224.972 | 226.439 | 227.972 | 50.021
2025-10-22 08:18 | 74176.195 | 86314.117 | -43157.059 | 0.86 | 0.85938 | 26973.162 | 22927.188 | 24275.846 | 31019.137 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 225.231 | 226.871 | 228.446 | 50.007
2025-10-22 08:19 | 82268.141 | 95754.727 | -45854.375 | 0.87 | 0.85915 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 31019.137 | 31019.137 | -16183.896 | -16183.896 | -13486.581 | 224.843 | 226.569 | 228.382 | 50.016
2025-10-22 08:20 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 31019.137 | 31019.137 | -17532.555 | -16183.896 | -13486.581 | 224.886 | 226.526 | 228.36 | 50.019
2025-10-22 08:21 | 84965.461 | 97103.383 | -47203.031 | 0.87 | 0.875 | 29670.479 | 25624.504 | 28321.82 | 35065.109 | 31019.137 | 31019.137 | -17532.555 | -16183.896 | -13486.581 | 224.799 | 226.526 | 228.123 | 50.001
2025-10-22 08:22 | 80919.484 | 94406.063 | -45854.375 | 0.86 | 0.85714 | 28321.82 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -17532.555 | -16183.896 | -13486.581 | 224.821 | 226.526 | 228.101 | 50.012
2025-10-22 08:23 | 74176.195 | 87662.773 | -44505.715 | 0.85 | 0.84615 | 26973.162 | 22927.188 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 225.468 | 227.044 | 228.489 | 50.011
2025-10-22 08:24 | 78222.172 | 89011.43 | -41808.402 | 0.88 | 0.87879 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 225.015 | 226.418 | 227.713 | 50.019
2025-10-22 08:25 | 75524.852 | 84965.461 | -39111.086 | 0.89 | 0.88889 | 25624.504 | 24275.846 | 25624.504 | 29670.479 | 26973.162 | 28321.82 | -13486.581 | -13486.581 | -12137.923 | 225.058 | 226.375 | 227.713 | 50.011
2025-10-22 08:26 | 78222.172 | 87662.773 | -40459.742 | 0.89 | 0.89231 | 26973.162 | 25624.504 | 26973.162 | 31019.137 | 28321.82 | 29670.479 | -14835.239 | -13486.581 | -12137.923 | 224.346 | 225.598 | 226.914 | 50.015
2025-10-22 08:27 | 78222.172 | 89011.43 | -40459.742 | 0.89 | 0.87879 | 26973.162 | 25624.504 | 26973.162 | 31019.137 | 28321.82 | 29670.479 | -14835.239 | -13486.581 | -12137.923 | 224.605 | 225.749 | 226.979 | 50.018
2025-10-22 08:28 | 79570.828 | 90360.094 | -41808.402 | 0.88 | 0.8806 | 26973.162 | 26973.162 | 25624.504 | 31019.137 | 31019.137 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 224.972 | 225.922 | 227.346 | 50.019
2025-10-22 08:29 | 76873.508 | 86314.117 | -39111.086 | 0.89 | 0.89062 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 29670.479 | 28321.82 | -13486.581 | -13486.581 | -12137.923 | 225.555 | 226.612 | 228.338 | 50.021
2025-10-22 08:30 | 84965.461 | 97103.383 | -45854.375 | 0.88 | 0.875 | 28321.82 | 29670.479 | 26973.162 | 32367.793 | 33716.453 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 225.49 | 226.396 | 229.007 | 50.021
2025-10-22 08:31 | 84965.461 | 97103.383 | -45854.375 | 0.87 | 0.875 | 28321.82 | 28321.82 | 26973.162 | 33716.453 | 33716.453 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 225.576 | 226.418 | 229.072 | 50.024
2025-10-22 08:32 | 87662.773 | 99800.695 | -47203.031 | 0.88 | 0.87838 | 29670.479 | 29670.479 | 28321.82 | 33716.453 | 35065.109 | 31019.137 | -16183.896 | -17532.555 | -12137.923 | 224.497 | 225.36 | 227.993 | 50.016
2025-10-22 08:33 | 86314.117 | 98452.039 | -47203.031 | 0.87 | 0.87671 | 29670.479 | 29670.479 | 28321.82 | 33716.453 | 33716.453 | 31019.137 | -17532.555 | -17532.555 | -12137.923 | 225.49 | 226.439 | 229.223 | 50.013
2025-10-22 08:34 | 83616.805 | 97103.383 | -47203.031 | 0.86 | 0.86111 | 28321.82 | 28321.82 | 26973.162 | 33716.453 | 33716.453 | 29670.479 | -17532.555 | -17532.555 | -12137.923 | 226.288 | 227.065 | 229.784 | 50.016
2025-10-22 08:35 | 83616.805 | 94406.063 | -44505.715 | 0.88 | 0.88571 | 26973.162 | 29670.479 | 26973.162 | 31019.137 | 33716.453 | 29670.479 | -14835.239 | -16183.896 | -12137.923 | 225.598 | 226.051 | 229.051 | 50.01
2025-10-22 08:36 | 75524.852 | 84965.461 | -37762.426 | 0.89 | 0.88889 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -13486.581 | -14835.239 | -10789.265 | 226.073 | 226.655 | 229.158 | 50.015
2025-10-22 08:37 | 78222.172 | 89011.43 | -41808.402 | 0.88 | 0.87879 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -14835.239 | -14835.239 | -10789.265 | 226.288 | 227.346 | 229.504 | 50.024
2025-10-22 08:38 | 70130.219 | 80919.484 | -41808.402 | 0.86 | 0.86667 | 24275.846 | 22927.188 | 22927.188 | 29670.479 | 26973.162 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 226.871 | 227.734 | 229.935 | 50.027
2025-10-22 08:39 | 67432.906 | 78222.172 | -37762.426 | 0.87 | 0.86207 | 24275.846 | 21578.529 | 21578.529 | 28321.82 | 25624.504 | 24275.846 | -13486.581 | -14835.239 | -9440.606 | 227.044 | 228.079 | 230.173 | 50.034
2025-10-22 08:40 | 75524.852 | 86314.117 | -43157.059 | 0.86 | 0.875 | 26973.162 | 22927.188 | 24275.846 | 31019.137 | 28321.82 | 26973.162 | -16183.896 | -14835.239 | -12137.923 | 226.806 | 228.123 | 229.935 | 50.045
2025-10-22 08:41 | 80919.484 | 93057.406 | -44505.715 | 0.87 | 0.86957 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 226.267 | 227.475 | 229.568 | 50.044
2025-10-22 08:42 | 86314.117 | 99800.695 | -48551.691 | 0.87 | 0.86486 | 31019.137 | 26973.162 | 28321.82 | 35065.109 | 32367.793 | 32367.793 | -17532.555 | -17532.555 | -13486.581 | 226.051 | 227.152 | 229.439 | 50.033
2025-10-22 08:43 | 83616.805 | 94406.063 | -45854.375 | 0.87 | 0.88571 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.533 | 226.72 | 228.835 | 50.023
2025-10-22 08:44 | 86314.117 | 97103.383 | -44505.715 | 0.88 | 0.88889 | 31019.137 | 26973.162 | 28321.82 | 35065.109 | 31019.137 | 31019.137 | -16183.896 | -16183.896 | -12137.923 | 226.267 | 227.82 | 229.482 | 50.043
2025-10-22 08:45 | 86314.117 | 98452.039 | -45854.375 | 0.88 | 0.87671 | 31019.137 | 26973.162 | 28321.82 | 35065.109 | 32367.793 | 31019.137 | -16183.896 | -16183.896 | -13486.581 | 226.332 | 228.123 | 229.59 | 50.046
2025-10-22 08:46 | 79570.828 | 91708.75 | -44505.715 | 0.87 | 0.86765 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 226.483 | 228.123 | 229.763 | 50.046
2025-10-22 08:47 | 80919.484 | 91708.75 | -43157.059 | 0.88 | 0.88235 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.857 | 227.669 | 228.964 | 50.04
2025-10-22 08:48 | 79570.828 | 91708.75 | -43157.059 | 0.88 | 0.86765 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 226.483 | 228.511 | 229.741 | 50.039
2025-10-22 08:49 | 79570.828 | 91708.75 | -43157.059 | 0.88 | 0.86765 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -14835.239 | -14835.239 | -12137.923 | 226.224 | 228.123 | 229.439 | 50.029
2025-10-22 08:50 | 80919.484 | 91708.75 | -43157.059 | 0.88 | 0.88235 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 226.288 | 227.95 | 229.245 | 50.04
2025-10-22 08:51 | 75524.852 | 87662.773 | -43157.059 | 0.86 | 0.86154 | 26973.162 | 22927.188 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 226.569 | 228.209 | 229.353 | 50.033
2025-10-22 08:52 | 78222.172 | 89011.43 | -41808.402 | 0.87 | 0.87879 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 227 | 228.77 | 229.935 | 50.028
2025-10-22 08:53 | 75524.852 | 86314.117 | -41808.402 | 0.87 | 0.875 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 28321.82 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 226.547 | 228.295 | 229.827 | 50.03
2025-10-22 08:54 | 79570.828 | 90360.094 | -43157.059 | 0.88 | 0.8806 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -14835.239 | -16183.896 | -12137.923 | 226.72 | 228.274 | 229.849 | 50.028
2025-10-22 08:55 | 79570.828 | 90360.094 | -43157.059 | 0.87 | 0.8806 | 26973.162 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.396 | 227.864 | 229.719 | 50.026
2025-10-22 08:56 | 76873.508 | 87662.773 | -43157.059 | 0.87 | 0.87692 | 26973.162 | 24275.846 | 24275.846 | 31019.137 | 29670.479 | 26973.162 | -16183.896 | -16183.896 | -12137.923 | 226.59 | 227.756 | 229.849 | 50.029
2025-10-22 08:57 | 70130.219 | 80919.484 | -40459.742 | 0.86 | 0.86667 | 24275.846 | 22927.188 | 22927.188 | 28321.82 | 26973.162 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 225.986 | 227.238 | 229.353 | 50.033
2025-10-22 08:58 | 70130.219 | 80919.484 | -39111.086 | 0.87 | 0.86667 | 22927.188 | 25624.504 | 22927.188 | 26973.162 | 29670.479 | 25624.504 | -13486.581 | -14835.239 | -12137.923 | 226.526 | 227.756 | 229.957 | 50.036
2025-10-22 08:59 | 68781.563 | 78222.172 | -36413.77 | 0.88 | 0.87931 | 21578.529 | 25624.504 | 21578.529 | 24275.846 | 28321.82 | 24275.846 | -12137.923 | -13486.581 | -10789.265 | 226.655 | 227.497 | 229.935 | 50.036
2025-10-22 09:00 | 72827.539 | 80919.484 | -35065.109 | 0.89 | 0.9 | 22927.188 | 26973.162 | 22927.188 | 25624.504 | 29670.479 | 25624.504 | -12137.923 | -13486.581 | -10789.265 | 226.202 | 227.087 | 229.676 | 50.034
2025-10-22 09:01 | 74176.195 | 84965.461 | -40459.742 | 0.88 | 0.87302 | 24275.846 | 26973.162 | 22927.188 | 28321.82 | 31019.137 | 25624.504 | -13486.581 | -14835.239 | -12137.923 | 225.878 | 227.044 | 229.115 | 50.016
2025-10-22 09:02 | 74176.195 | 83616.805 | -37762.426 | 0.89 | 0.8871 | 24275.846 | 25624.504 | 24275.846 | 28321.82 | 28321.82 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 224.454 | 225.555 | 227.475 | 49.992
2025-10-22 09:03 | 76873.508 | 84965.461 | -37762.426 | 0.89 | 0.90476 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 223.979 | 225.015 | 227.13 | 49.972
2025-10-22 09:04 | 75524.852 | 86314.117 | -40459.742 | 0.87 | 0.875 | 26973.162 | 24275.846 | 24275.846 | 31019.137 | 28321.82 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 223.31 | 224.756 | 226.288 | 49.968
2025-10-22 09:05 | 75524.852 | 86314.117 | -40459.742 | 0.88 | 0.875 | 26973.162 | 22927.188 | 25624.504 | 31019.137 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 223.138 | 224.886 | 225.986 | 49.981
2025-10-22 09:06 | 71478.875 | 82268.141 | -40459.742 | 0.87 | 0.86885 | 25624.504 | 21578.529 | 24275.846 | 29670.479 | 26973.162 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 222.577 | 224.087 | 225.209 | 50.006
2025-10-22 09:07 | 68781.563 | 76873.508 | -33716.453 | 0.9 | 0.89474 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 223.159 | 224.368 | 225.404 | 49.996
2025-10-22 09:08 | 71478.875 | 79570.828 | -35065.109 | 0.89 | 0.89831 | 24275.846 | 22927.188 | 24275.846 | 26973.162 | 25624.504 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 223.505 | 225.058 | 226.18 | 50
2025-10-22 09:09 | 66084.242 | 74176.195 | -35065.109 | 0.88 | 0.89091 | 22927.188 | 21578.529 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 224.346 | 225.835 | 226.677 | 50.002
2025-10-22 09:10 | 64735.586 | 72827.539 | -33716.453 | 0.89 | 0.88889 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 224.066 | 225.555 | 226.504 | 50.012
2025-10-22 09:11 | 66084.242 | 74176.195 | -33716.453 | 0.89 | 0.89091 | 22927.188 | 20229.871 | 22927.188 | 26973.162 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 223.31 | 224.174 | 225.468 | 50.024
2025-10-22 09:12 | 66084.242 | 74176.195 | -33716.453 | 0.89 | 0.89091 | 22927.188 | 20229.871 | 22927.188 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 223.634 | 224.67 | 225.965 | 50.025
2025-10-22 09:13 | 63386.93 | 72827.539 | -33716.453 | 0.89 | 0.87037 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 22927.188 | 22927.188 | -12137.923 | -10789.265 | -9440.606 | 223.591 | 224.497 | 225.77 | 50.017
2025-10-22 09:14 | 60689.613 | 67432.906 | -29670.479 | 0.89 | 0.9 | 20229.871 | 18881.213 | 20229.871 | 22927.188 | 21578.529 | 21578.529 | -10789.265 | -10789.265 | -9440.606 | 224.454 | 225.576 | 226.936 | 50.018
2025-10-22 09:15 | 60689.613 | 67432.906 | -28321.82 | 0.91 | 0.9 | 20229.871 | 20229.871 | 20229.871 | 21578.529 | 22927.188 | 22927.188 | -9440.606 | -9440.606 | -9440.606 | 224.54 | 225.814 | 227.108 | 50.004
2025-10-22 09:16 | 59340.957 | 64735.586 | -26973.162 | 0.91 | 0.91667 | 20229.871 | 20229.871 | 20229.871 | 21578.529 | 21578.529 | 21578.529 | -9440.606 | -8091.948 | -8091.948 | 223.915 | 224.648 | 226.094 | 49.986
2025-10-22 09:17 | 62038.273 | 67432.906 | -28321.82 | 0.91 | 0.92 | 20229.871 | 21578.529 | 20229.871 | 21578.529 | 22927.188 | 22927.188 | -9440.606 | -9440.606 | -9440.606 | 223.807 | 224.433 | 226.137 | 49.992
2025-10-22 09:18 | 62038.273 | 67432.906 | -28321.82 | 0.91 | 0.92 | 20229.871 | 21578.529 | 20229.871 | 21578.529 | 24275.846 | 21578.529 | -9440.606 | -9440.606 | -9440.606 | 223.915 | 224.864 | 226.353 | 49.981
2025-10-22 09:19 | 62038.273 | 67432.906 | -26973.162 | 0.91 | 0.92 | 20229.871 | 21578.529 | 20229.871 | 21578.529 | 22927.188 | 21578.529 | -9440.606 | -9440.606 | -8091.948 | 224.044 | 224.605 | 226.288 | 49.98
2025-10-22 09:20 | 66084.242 | 72827.539 | -31019.137 | 0.9 | 0.90741 | 21578.529 | 22927.188 | 21578.529 | 24275.846 | 25624.504 | 22927.188 | -10789.265 | -10789.265 | -9440.606 | 223.828 | 224.584 | 226.526 | 49.99
2025-10-22 09:21 | 64735.586 | 71478.875 | -29670.479 | 0.91 | 0.90566 | 20229.871 | 22927.188 | 21578.529 | 22927.188 | 24275.846 | 22927.188 | -9440.606 | -9440.606 | -9440.606 | 224.13 | 224.821 | 226.72 | 50.005
2025-10-22 09:22 | 66084.242 | 72827.539 | -29670.479 | 0.91 | 0.90741 | 21578.529 | 22927.188 | 21578.529 | 24275.846 | 25624.504 | 24275.846 | -10789.265 | -10789.265 | -9440.606 | 224.152 | 224.756 | 226.763 | 50.014
2025-10-22 09:23 | 74176.195 | 82268.141 | -36413.77 | 0.9 | 0.90164 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -12137.923 | -12137.923 | -10789.265 | 223.807 | 224.756 | 226.871 | 50.004
2025-10-22 09:24 | 74176.195 | 82268.141 | -36413.77 | 0.9 | 0.90164 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -12137.923 | -10789.265 | 223.03 | 223.785 | 226.029 | 50.013
2025-10-22 09:25 | 76873.508 | 86314.117 | -39111.086 | 0.89 | 0.89062 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 29670.479 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 223.375 | 224.584 | 226.073 | 50.013
2025-10-22 09:26 | 75524.852 | 84965.461 | -37762.426 | 0.89 | 0.88889 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 223.699 | 224.476 | 226.418 | 50.021
2025-10-22 09:27 | 76873.508 | 86314.117 | -37762.426 | 0.89 | 0.89062 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 29670.479 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 223.159 | 223.677 | 225.641 | 50.02
2025-10-22 09:28 | 83616.805 | 94406.063 | -44505.715 | 0.88 | 0.88571 | 28321.82 | 28321.82 | 26973.162 | 32367.793 | 32367.793 | 29670.479 | -14835.239 | -16183.896 | -12137.923 | 223.246 | 224.325 | 226.353 | 50.02
2025-10-22 09:29 | 71478.875 | 82268.141 | -40459.742 | 0.87 | 0.86885 | 25624.504 | 22927.188 | 22927.188 | 28321.82 | 28321.82 | 25624.504 | -14835.239 | -16183.896 | -10789.265 | 224.087 | 225.274 | 227.022 | 50.017
2025-10-22 09:30 | 66084.242 | 76873.508 | -37762.426 | 0.86 | 0.85965 | 22927.188 | 21578.529 | 21578.529 | 26973.162 | 25624.504 | 22927.188 | -13486.581 | -14835.239 | -9440.606 | 224.109 | 225.015 | 227.152 | 50.018
2025-10-22 09:31 | 62038.273 | 71478.875 | -35065.109 | 0.86 | 0.86792 | 21578.529 | 20229.871 | 20229.871 | 25624.504 | 24275.846 | 21578.529 | -13486.581 | -13486.581 | -9440.606 | 224.972 | 225.814 | 227.907 | 50.001
2025-10-22 09:32 | 62038.273 | 70130.219 | -31019.137 | 0.89 | 0.88462 | 21578.529 | 20229.871 | 21578.529 | 24275.846 | 22927.188 | 22927.188 | -12137.923 | -10789.265 | -9440.606 | 224.454 | 225.684 | 227.367 | 49.975
2025-10-22 09:33 | 59340.957 | 67432.906 | -31019.137 | 0.89 | 0.88 | 20229.871 | 18881.213 | 20229.871 | 22927.188 | 21578.529 | 21578.529 | -10789.265 | -10789.265 | -9440.606 | 225.037 | 226.116 | 227.842 | 49.975
2025-10-22 09:34 | 60689.613 | 68781.563 | -31019.137 | 0.89 | 0.88235 | 21578.529 | 18881.213 | 20229.871 | 24275.846 | 21578.529 | 22927.188 | -10789.265 | -10789.265 | -9440.606 | 225.641 | 226.849 | 228.446 | 49.975
2025-10-22 09:35 | 62038.273 | 70130.219 | -32367.793 | 0.88 | 0.88462 | 21578.529 | 20229.871 | 20229.871 | 24275.846 | 22927.188 | 22927.188 | -12137.923 | -10789.265 | -9440.606 | 225.706 | 227.281 | 228.446 | 49.978
2025-10-22 09:36 | 62038.273 | 70130.219 | -32367.793 | 0.88 | 0.88462 | 21578.529 | 20229.871 | 20229.871 | 24275.846 | 22927.188 | 22927.188 | -12137.923 | -10789.265 | -9440.606 | 225.576 | 226.957 | 227.95 | 49.988
2025-10-22 09:37 | 56643.641 | 63386.93 | -29670.479 | 0.89 | 0.89362 | 20229.871 | 17532.555 | 18881.213 | 21578.529 | 20229.871 | 20229.871 | -10789.265 | -9440.606 | -8091.948 | 225.339 | 226.785 | 227.583 | 50.01
2025-10-22 09:38 | 59340.957 | 67432.906 | -31019.137 | 0.88 | 0.88 | 20229.871 | 18881.213 | 20229.871 | 24275.846 | 21578.529 | 21578.529 | -10789.265 | -10789.265 | -9440.606 | 226.051 | 227.518 | 228.382 | 50.023
2025-10-22 09:39 | 59340.957 | 66084.242 | -29670.479 | 0.89 | 0.89796 | 20229.871 | 18881.213 | 20229.871 | 22927.188 | 21578.529 | 21578.529 | -10789.265 | -10789.265 | -9440.606 | 226.245 | 227.648 | 228.576 | 50.022
2025-10-22 09:40 | 60689.613 | 67432.906 | -31019.137 | 0.89 | 0.9 | 20229.871 | 18881.213 | 20229.871 | 24275.846 | 21578.529 | 22927.188 | -10789.265 | -10789.265 | -9440.606 | 225.253 | 226.677 | 227.691 | 50.028
2025-10-22 09:41 | 57992.297 | 64735.586 | -29670.479 | 0.89 | 0.89583 | 20229.871 | 18881.213 | 18881.213 | 22927.188 | 21578.529 | 21578.529 | -10789.265 | -10789.265 | -9440.606 | 225.986 | 228.015 | 228.792 | 50.019
2025-10-22 09:42 | 59340.957 | 66084.242 | -29670.479 | 0.89 | 0.89796 | 20229.871 | 18881.213 | 20229.871 | 22927.188 | 21578.529 | 21578.529 | -10789.265 | -10789.265 | -9440.606 | 225.598 | 227.54 | 228.295 | 50.018
2025-10-22 09:43 | 59340.957 | 67432.906 | -31019.137 | 0.89 | 0.88 | 20229.871 | 20229.871 | 18881.213 | 22927.188 | 22927.188 | 21578.529 | -10789.265 | -10789.265 | -8091.948 | 225.943 | 227.281 | 228.446 | 50.019
2025-10-22 09:44 | 60689.613 | 67432.906 | -29670.479 | 0.89 | 0.9 | 20229.871 | 20229.871 | 20229.871 | 22927.188 | 22927.188 | 21578.529 | -10789.265 | -10789.265 | -8091.948 | 225.943 | 227.044 | 228.187 | 50.025
2025-10-22 09:45 | 60689.613 | 68781.563 | -31019.137 | 0.89 | 0.88235 | 20229.871 | 20229.871 | 20229.871 | 22927.188 | 22927.188 | 21578.529 | -10789.265 | -10789.265 | -8091.948 | 225.641 | 226.957 | 227.972 | 50.023
2025-10-22 09:46 | 60689.613 | 67432.906 | -29670.479 | 0.9 | 0.9 | 20229.871 | 20229.871 | 20229.871 | 22927.188 | 22927.188 | 21578.529 | -10789.265 | -10789.265 | -8091.948 | 225.835 | 227.108 | 227.691 | 50.011
2025-10-22 09:47 | 63386.93 | 71478.875 | -31019.137 | 0.9 | 0.88679 | 21578.529 | 21578.529 | 21578.529 | 24275.846 | 24275.846 | 22927.188 | -10789.265 | -10789.265 | -8091.948 | 225.663 | 226.655 | 227.583 | 50
2025-10-22 09:48 | 60689.613 | 67432.906 | -29670.479 | 0.89 | 0.9 | 20229.871 | 20229.871 | 20229.871 | 22927.188 | 22927.188 | 21578.529 | -10789.265 | -10789.265 | -8091.948 | 226.59 | 227.864 | 228.856 | 49.989
2025-10-22 09:49 | 57992.297 | 64735.586 | -29670.479 | 0.89 | 0.89583 | 18881.213 | 18881.213 | 18881.213 | 21578.529 | 21578.529 | 20229.871 | -10789.265 | -10789.265 | -8091.948 | 226.957 | 228.166 | 229.309 | 49.991
2025-10-22 09:50 | 59340.957 | 66084.242 | -29670.479 | 0.89 | 0.89796 | 20229.871 | 18881.213 | 18881.213 | 22927.188 | 22927.188 | 21578.529 | -10789.265 | -10789.265 | -8091.948 | 226.612 | 227.281 | 228.468 | 49.992
2025-10-22 09:51 | 66084.242 | 72827.539 | -32367.793 | 0.89 | 0.90741 | 21578.529 | 22927.188 | 21578.529 | 24275.846 | 25624.504 | 22927.188 | -10789.265 | -12137.923 | -8091.948 | 226.655 | 227.152 | 228.468 | 50.008
2025-10-22 09:52 | 63386.93 | 70130.219 | -31019.137 | 0.89 | 0.90385 | 21578.529 | 21578.529 | 20229.871 | 22927.188 | 24275.846 | 21578.529 | -10789.265 | -12137.923 | -9440.606 | 226.655 | 227.993 | 228.511 | 50.01
2025-10-22 09:53 | 60689.613 | 68781.563 | -29670.479 | 0.89 | 0.88235 | 20229.871 | 21578.529 | 18881.213 | 22927.188 | 24275.846 | 21578.529 | -10789.265 | -12137.923 | -8091.948 | 226.957 | 228.166 | 229.309 | 50.016
2025-10-22 09:54 | 59340.957 | 67432.906 | -31019.137 | 0.89 | 0.88 | 20229.871 | 20229.871 | 18881.213 | 22927.188 | 22927.188 | 21578.529 | -10789.265 | -12137.923 | -8091.948 | 227.475 | 228.274 | 230.151 | 50.018
2025-10-22 09:55 | 60689.613 | 68781.563 | -31019.137 | 0.89 | 0.88235 | 20229.871 | 21578.529 | 20229.871 | 22927.188 | 24275.846 | 21578.529 | -10789.265 | -12137.923 | -8091.948 | 227.324 | 228.252 | 230.022 | 50.025
2025-10-22 09:56 | 59340.957 | 66084.242 | -31019.137 | 0.88 | 0.89796 | 20229.871 | 20229.871 | 18881.213 | 22927.188 | 22927.188 | 20229.871 | -10789.265 | -12137.923 | -8091.948 | 228.274 | 229.137 | 230.842 | 50.019
2025-10-22 09:57 | 56643.641 | 64735.586 | -29670.479 | 0.88 | 0.875 | 20229.871 | 18881.213 | 18881.213 | 22927.188 | 21578.529 | 20229.871 | -10789.265 | -10789.265 | -8091.948 | 227.993 | 228.986 | 230.453 | 50.025
2025-10-22 09:58 | 56643.641 | 63386.93 | -29670.479 | 0.89 | 0.89362 | 20229.871 | 17532.555 | 18881.213 | 21578.529 | 21578.529 | 20229.871 | -10789.265 | -10789.265 | -8091.948 | 227.842 | 229.115 | 230.065 | 50.026
2025-10-22 09:59 | 55294.98 | 63386.93 | -31019.137 | 0.87 | 0.87234 | 18881.213 | 17532.555 | 18881.213 | 22927.188 | 20229.871 | 20229.871 | -10789.265 | -10789.265 | -9440.606 | 229.051 | 229.827 | 231.489 | 50.017
2025-10-22 10:00 | 52597.664 | 59340.957 | -26973.162 | 0.88 | 0.88636 | 18881.213 | 16183.896 | 17532.555 | 21578.529 | 18881.213 | 18881.213 | -10789.265 | -9440.606 | -8091.948 | 229.612 | 230.216 | 231.618 | 50.026
2025-10-22 10:01 | 52597.664 | 59340.957 | -25624.504 | 0.89 | 0.88636 | 18881.213 | 16183.896 | 17532.555 | 21578.529 | 18881.213 | 18881.213 | -9440.606 | -9440.606 | -6743.291 | 229.115 | 229.914 | 231.101 | 50.001
2025-10-22 10:02 | 47203.031 | 53946.324 | -24275.846 | 0.89 | 0.875 | 17532.555 | 14835.239 | 16183.896 | 18881.213 | 17532.555 | 17532.555 | -9440.606 | -8091.948 | -6743.291 | 226.029 | 226.634 | 228.123 | 49.971
2025-10-22 10:03 | 33716.453 | 39111.086 | -18881.213 | 0.87 | 0.86207 | 12137.923 | 9440.606 | 10789.265 | 14835.239 | 12137.923 | 12137.923 | -6743.291 | -6743.291 | -4045.974 | 226.439 | 227 | 228.187 | 49.969
2025-10-22 10:04 | 29670.479 | 32367.793 | -14835.239 | 0.88 | 0.91667 | 10789.265 | 8091.948 | 9440.606 | 12137.923 | 10789.265 | 10789.265 | -5394.632 | -5394.632 | -4045.974 | 226.979 | 228.036 | 228.727 | 49.971
2025-10-22 10:05 | 29670.479 | 32367.793 | -14835.239 | 0.89 | 0.91667 | 10789.265 | 8091.948 | 9440.606 | 12137.923 | 10789.265 | 10789.265 | -5394.632 | -5394.632 | -4045.974 | 228.144 | 229.331 | 229.784 | 49.976
2025-10-22 10:06 | 28321.82 | 31019.137 | -10789.265 | 0.94 | 0.91304 | 9440.606 | 9440.606 | 9440.606 | 9440.606 | 10789.265 | 10789.265 | -4045.974 | -4045.974 | -4045.974 | 228.338 | 229.849 | 229.849 | 49.985
2025-10-22 10:07 | 26973.162 | 28321.82 | -9440.606 | 0.95 | 0.95238 | 8091.948 | 9440.606 | 9440.606 | 9440.606 | 9440.606 | 9440.606 | -2697.316 | -2697.316 | -2697.316 | 227.842 | 229.806 | 228.943 | 49.984
2025-10-22 10:08 | 26973.162 | 28321.82 | -8091.948 | 0.95 | 0.95238 | 8091.948 | 9440.606 | 9440.606 | 9440.606 | 9440.606 | 9440.606 | -2697.316 | -2697.316 | -2697.316 | 227.238 | 228.684 | 228.295 | 49.995
2025-10-22 10:09 | 25624.504 | 26973.162 | -8091.948 | 0.96 | 0.95 | 8091.948 | 9440.606 | 9440.606 | 9440.606 | 9440.606 | 9440.606 | -2697.316 | -2697.316 | -2697.316 | 227.842 | 229.374 | 228.835 | 50.007
2025-10-22 10:10 | 25624.504 | 26973.162 | -8091.948 | 0.96 | 0.95 | 8091.948 | 9440.606 | 8091.948 | 8091.948 | 9440.606 | 9440.606 | -2697.316 | -2697.316 | -2697.316 | 228.986 | 230.928 | 230.432 | 50.019
2025-10-22 10:11 | 26973.162 | 28321.82 | -8091.948 | 0.96 | 0.95238 | 8091.948 | 9440.606 | 9440.606 | 8091.948 | 10789.265 | 9440.606 | -2697.316 | -2697.316 | -2697.316 | 228.943 | 230.647 | 230.712 | 50.024
2025-10-22 10:12 | 28321.82 | 29670.479 | -8091.948 | 0.96 | 0.95455 | 8091.948 | 10789.265 | 9440.606 | 8091.948 | 10789.265 | 9440.606 | -2697.316 | -2697.316 | -2697.316 | 228.554 | 230.259 | 230.194 | 50.029
2025-10-22 10:13 | 28321.82 | 29670.479 | -8091.948 | 0.95 | 0.95455 | 9440.606 | 10789.265 | 9440.606 | 9440.606 | 10789.265 | 9440.606 | -2697.316 | -2697.316 | -2697.316 | 228.209 | 229.266 | 229.504 | 50.023
2025-10-22 10:14 | 29670.479 | 31019.137 | -9440.606 | 0.95 | 0.95652 | 9440.606 | 10789.265 | 9440.606 | 9440.606 | 10789.265 | 9440.606 | -2697.316 | -2697.316 | -2697.316 | 228.662 | 229.158 | 229.633 | 50.028
2025-10-22 10:15 | 28321.82 | 29670.479 | -8091.948 | 0.96 | 0.95455 | 8091.948 | 10789.265 | 9440.606 | 9440.606 | 10789.265 | 9440.606 | -2697.316 | -2697.316 | -2697.316 | 228.101 | 229.245 | 229.633 | 50.018
2025-10-22 10:16 | 26973.162 | 28321.82 | -8091.948 | 0.96 | 0.95238 | 8091.948 | 10789.265 | 8091.948 | 8091.948 | 10789.265 | 9440.606 | -2697.316 | -2697.316 | -2697.316 | 227.864 | 229.137 | 229.374 | 50.001
2025-10-22 10:17 | 26973.162 | 28321.82 | -8091.948 | 0.96 | 0.95238 | 8091.948 | 10789.265 | 8091.948 | 8091.948 | 10789.265 | 9440.606 | -2697.316 | -2697.316 | -2697.316 | 228.209 | 230.022 | 229.676 | 49.981
2025-10-22 10:18 | 28321.82 | 29670.479 | -8091.948 | 0.95 | 0.95455 | 8091.948 | 10789.265 | 9440.606 | 8091.948 | 10789.265 | 9440.606 | -2697.316 | -2697.316 | -2697.316 | 228.727 | 230.432 | 230.302 | 49.98
2025-10-22 10:19 | 26973.162 | 28321.82 | -8091.948 | 0.96 | 0.95238 | 8091.948 | 9440.606 | 8091.948 | 8091.948 | 10789.265 | 9440.606 | -2697.316 | -2697.316 | -2697.316 | 228.878 | 230.194 | 230.496 | 49.984
2025-10-22 10:20 | 29670.479 | 31019.137 | -9440.606 | 0.95 | 0.95652 | 9440.606 | 10789.265 | 9440.606 | 9440.606 | 12137.923 | 9440.606 | -2697.316 | -4045.974 | -2697.316 | 229.331 | 230.539 | 231.101 | 49.989
2025-10-22 10:21 | 32367.793 | 35065.109 | -10789.265 | 0.94 | 0.92308 | 9440.606 | 12137.923 | 10789.265 | 10789.265 | 13486.581 | 10789.265 | -4045.974 | -4045.974 | -2697.316 | 228.964 | 229.202 | 230.281 | 49.992
2025-10-22 10:22 | 29670.479 | 31019.137 | -9440.606 | 0.94 | 0.95652 | 9440.606 | 10789.265 | 9440.606 | 9440.606 | 12137.923 | 9440.606 | -2697.316 | -4045.974 | -2697.316 | 228.446 | 228.597 | 229.957 | 50.013
2025-10-22 10:23 | 43157.059 | 45854.375 | -17532.555 | 0.92 | 0.94118 | 14835.239 | 14835.239 | 13486.581 | 16183.896 | 16183.896 | 14835.239 | -6743.291 | -6743.291 | -4045.974 | 228.166 | 228.705 | 230.324 | 50.029
2025-10-22 10:24 | 44505.715 | 48551.691 | -18881.213 | 0.91 | 0.91667 | 14835.239 | 14835.239 | 14835.239 | 17532.555 | 16183.896 | 14835.239 | -6743.291 | -8091.948 | -4045.974 | 226.547 | 226.483 | 228.684 | 50.038
2025-10-22 10:25 | 47203.031 | 52597.664 | -20229.871 | 0.92 | 0.89744 | 16183.896 | 16183.896 | 14835.239 | 17532.555 | 17532.555 | 16183.896 | -8091.948 | -8091.948 | -4045.974 | 226.72 | 226.655 | 228.878 | 50.035
2025-10-22 10:26 | 48551.691 | 52597.664 | -20229.871 | 0.91 | 0.92308 | 16183.896 | 16183.896 | 14835.239 | 17532.555 | 18881.213 | 16183.896 | -6743.291 | -8091.948 | -5394.632 | 227.691 | 228.878 | 230.539 | 50.035
2025-10-22 10:27 | 45854.375 | 49900.348 | -20229.871 | 0.92 | 0.91892 | 16183.896 | 14835.239 | 14835.239 | 17532.555 | 16183.896 | 16183.896 | -6743.291 | -6743.291 | -5394.632 | 226.31 | 227.842 | 228.835 | 50.033
2025-10-22 10:28 | 48551.691 | 52597.664 | -21578.529 | 0.91 | 0.92308 | 17532.555 | 14835.239 | 16183.896 | 18881.213 | 16183.896 | 17532.555 | -8091.948 | -8091.948 | -5394.632 | 226.893 | 227.907 | 229.115 | 50.02
2025-10-22 10:29 | 47203.031 | 52597.664 | -21578.529 | 0.91 | 0.89744 | 17532.555 | 14835.239 | 16183.896 | 18881.213 | 16183.896 | 17532.555 | -8091.948 | -8091.948 | -5394.632 | 225.9 | 226.547 | 227.928 | 50.022
2025-10-22 10:30 | 45854.375 | 51249.008 | -20229.871 | 0.91 | 0.89474 | 16183.896 | 13486.581 | 16183.896 | 18881.213 | 16183.896 | 16183.896 | -8091.948 | -6743.291 | -5394.632 | 224.843 | 225.382 | 226.893 | 50.026
2025-10-22 10:31 | 47203.031 | 51249.008 | -21578.529 | 0.9 | 0.92105 | 16183.896 | 13486.581 | 16183.896 | 18881.213 | 16183.896 | 17532.555 | -9440.606 | -8091.948 | -5394.632 | 225.145 | 225.166 | 227.842 | 50.022
2025-10-22 10:32 | 49900.348 | 53946.324 | -20229.871 | 0.92 | 0.925 | 17532.555 | 14835.239 | 17532.555 | 18881.213 | 16183.896 | 17532.555 | -8091.948 | -6743.291 | -5394.632 | 225.835 | 226.504 | 228.489 | 50.018
2025-10-22 10:33 | 49900.348 | 53946.324 | -21578.529 | 0.92 | 0.925 | 17532.555 | 14835.239 | 17532.555 | 18881.213 | 16183.896 | 17532.555 | -8091.948 | -6743.291 | -5394.632 | 225.447 | 226.008 | 227.799 | 50.022
2025-10-22 10:34 | 48551.691 | 52597.664 | -20229.871 | 0.92 | 0.92308 | 17532.555 | 14835.239 | 16183.896 | 18881.213 | 16183.896 | 17532.555 | -8091.948 | -6743.291 | -5394.632 | 225.512 | 226.137 | 227.648 | 50.021
2025-10-22 10:35 | 44505.715 | 48551.691 | -18881.213 | 0.91 | 0.91667 | 16183.896 | 13486.581 | 14835.239 | 17532.555 | 14835.239 | 16183.896 | -8091.948 | -6743.291 | -5394.632 | 226.008 | 226.763 | 228.079 | 50.026
2025-10-22 10:36 | 49900.348 | 55294.98 | -21578.529 | 0.91 | 0.90244 | 17532.555 | 14835.239 | 16183.896 | 20229.871 | 17532.555 | 17532.555 | -8091.948 | -8091.948 | -5394.632 | 226.029 | 226.828 | 228.058 | 50.033
2025-10-22 10:37 | 49900.348 | 53946.324 | -21578.529 | 0.91 | 0.925 | 17532.555 | 16183.896 | 16183.896 | 18881.213 | 17532.555 | 17532.555 | -8091.948 | -8091.948 | -5394.632 | 225.209 | 226.763 | 227.475 | 50.027
2025-10-22 10:38 | 51249.008 | 56643.641 | -21578.529 | 0.92 | 0.90476 | 17532.555 | 17532.555 | 16183.896 | 18881.213 | 18881.213 | 17532.555 | -8091.948 | -8091.948 | -5394.632 | 225.404 | 226.483 | 227.799 | 50.042
2025-10-22 10:39 | 51249.008 | 55294.98 | -21578.529 | 0.92 | 0.92683 | 17532.555 | 17532.555 | 16183.896 | 18881.213 | 18881.213 | 17532.555 | -8091.948 | -8091.948 | -5394.632 | 225.706 | 226.72 | 228.23 | 50.035
2025-10-22 10:40 | 49900.348 | 55294.98 | -21578.529 | 0.92 | 0.90244 | 17532.555 | 17532.555 | 16183.896 | 18881.213 | 18881.213 | 17532.555 | -8091.948 | -8091.948 | -5394.632 | 224.864 | 226.288 | 227.367 | 50.034
2025-10-22 10:41 | 44505.715 | 48551.691 | -18881.213 | 0.91 | 0.91667 | 14835.239 | 14835.239 | 13486.581 | 16183.896 | 16183.896 | 14835.239 | -6743.291 | -8091.948 | -5394.632 | 224.929 | 225.986 | 227 | 50.037
2025-10-22 10:42 | 45854.375 | 49900.348 | -20229.871 | 0.91 | 0.91892 | 16183.896 | 16183.896 | 14835.239 | 17532.555 | 17532.555 | 14835.239 | -6743.291 | -8091.948 | -5394.632 | 224.325 | 225.814 | 226.31 | 50.047
2025-10-22 10:43 | 48551.691 | 53946.324 | -20229.871 | 0.92 | 0.9 | 16183.896 | 17532.555 | 16183.896 | 17532.555 | 18881.213 | 17532.555 | -6743.291 | -6743.291 | -6743.291 | 224.368 | 225.922 | 226.698 | 50.032
2025-10-22 10:44 | 53946.324 | 57992.297 | -22927.188 | 0.92 | 0.93023 | 17532.555 | 18881.213 | 17532.555 | 18881.213 | 20229.871 | 18881.213 | -6743.291 | -8091.948 | -6743.291 | 223.548 | 224.843 | 225.9 | 50.036
2025-10-22 10:45 | 55294.98 | 60689.613 | -24275.846 | 0.92 | 0.91111 | 18881.213 | 18881.213 | 18881.213 | 20229.871 | 20229.871 | 20229.871 | -8091.948 | -8091.948 | -8091.948 | 223.31 | 224.886 | 226.029 | 50.025
2025-10-22 10:46 | 56643.641 | 63386.93 | -28321.82 | 0.89 | 0.89362 | 20229.871 | 18881.213 | 18881.213 | 21578.529 | 21578.529 | 20229.871 | -9440.606 | -9440.606 | -8091.948 | 223.462 | 225.598 | 226.31 | 50.024
2025-10-22 10:47 | 59340.957 | 66084.242 | -28321.82 | 0.9 | 0.89796 | 20229.871 | 18881.213 | 20229.871 | 22927.188 | 21578.529 | 21578.529 | -10789.265 | -9440.606 | -8091.948 | 227.475 | 228.511 | 230.065 | 50.014
2025-10-22 10:48 | 64735.586 | 72827.539 | -33716.453 | 0.89 | 0.88889 | 22927.188 | 20229.871 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 226.828 | 227.95 | 229.676 | 50.024
2025-10-22 10:49 | 71478.875 | 79570.828 | -36413.77 | 0.89 | 0.89831 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 227.842 | 229.439 | 230.863 | 50.03
2025-10-22 10:50 | 67432.906 | 76873.508 | -35065.109 | 0.89 | 0.87719 | 22927.188 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 228.252 | 229.072 | 230.949 | 50.026
2025-10-22 10:51 | 70130.219 | 78222.172 | -36413.77 | 0.88 | 0.89655 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 228.166 | 228.792 | 230.647 | 50.019
2025-10-22 10:52 | 70130.219 | 80919.484 | -39111.086 | 0.87 | 0.86667 | 24275.846 | 22927.188 | 22927.188 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 228.792 | 230.173 | 231.511 | 50.02
2025-10-22 10:53 | 75524.852 | 84965.461 | -40459.742 | 0.88 | 0.88889 | 25624.504 | 24275.846 | 25624.504 | 29670.479 | 28321.82 | 28321.82 | -14835.239 | -13486.581 | -12137.923 | 227.432 | 228.856 | 230.302 | 50.021
2025-10-22 10:54 | 70130.219 | 82268.141 | -43157.059 | 0.84 | 0.85246 | 24275.846 | 22927.188 | 22927.188 | 28321.82 | 28321.82 | 25624.504 | -16183.896 | -16183.896 | -12137.923 | 226.504 | 227.389 | 229.568 | 50.03
2025-10-22 10:55 | 64735.586 | 75524.852 | -39111.086 | 0.85 | 0.85714 | 21578.529 | 21578.529 | 20229.871 | 25624.504 | 25624.504 | 22927.188 | -13486.581 | -14835.239 | -10789.265 | 227.713 | 228.317 | 230.82 | 50.035
2025-10-22 10:56 | 76873.508 | 89011.43 | -43157.059 | 0.87 | 0.86364 | 26973.162 | 25624.504 | 24275.846 | 31019.137 | 29670.479 | 26973.162 | -14835.239 | -16183.896 | -10789.265 | 227.799 | 228.511 | 230.647 | 50.038
2025-10-22 10:57 | 83616.805 | 95754.727 | -45854.375 | 0.87 | 0.87324 | 29670.479 | 26973.162 | 26973.162 | 33716.453 | 32367.793 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 227.13 | 227.303 | 229.806 | 50.044
2025-10-22 10:58 | 76873.508 | 89011.43 | -44505.715 | 0.87 | 0.86364 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 227.41 | 227.842 | 230.496 | 50.054
2025-10-22 10:59 | 78222.172 | 91708.75 | -47203.031 | 0.85 | 0.85294 | 26973.162 | 25624.504 | 25624.504 | 31019.137 | 31019.137 | 28321.82 | -16183.896 | -17532.555 | -12137.923 | 227.281 | 227.885 | 230.691 | 50.049
2025-10-22 11:00 | 79570.828 | 93057.406 | -47203.031 | 0.86 | 0.85507 | 26973.162 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -17532.555 | -13486.581 | 227.734 | 228.576 | 230.798 | 50.034
2025-10-22 11:01 | 78222.172 | 91708.75 | -47203.031 | 0.86 | 0.85294 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -17532.555 | -13486.581 | 227.713 | 228.597 | 230.432 | 50.014
2025-10-22 11:02 | 74176.195 | 86314.117 | -41808.402 | 0.87 | 0.85938 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 29670.479 | 26973.162 | -14835.239 | -14835.239 | -12137.923 | 227.044 | 227.799 | 229.719 | 50.009
2025-10-22 11:03 | 71478.875 | 82268.141 | -39111.086 | 0.88 | 0.86885 | 24275.846 | 24275.846 | 22927.188 | 28321.82 | 28321.82 | 25624.504 | -13486.581 | -13486.581 | -12137.923 | 226.353 | 227.173 | 228.964 | 49.99
2025-10-22 11:04 | 68781.563 | 79570.828 | -39111.086 | 0.87 | 0.86441 | 22927.188 | 22927.188 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -13486.581 | -13486.581 | -12137.923 | 226.547 | 227.303 | 229.245 | 50.005
2025-10-22 11:05 | 71478.875 | 82268.141 | -40459.742 | 0.87 | 0.86885 | 24275.846 | 24275.846 | 22927.188 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -14835.239 | -12137.923 | 226.698 | 227.518 | 229.504 | 49.998
2025-10-22 11:06 | 67432.906 | 78222.172 | -37762.426 | 0.87 | 0.86207 | 22927.188 | 21578.529 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 226.957 | 227.669 | 229.094 | 50.011
2025-10-22 11:07 | 70130.219 | 80919.484 | -39111.086 | 0.87 | 0.86667 | 24275.846 | 22927.188 | 22927.188 | 28321.82 | 26973.162 | 25624.504 | -13486.581 | -13486.581 | -12137.923 | 227.108 | 227.864 | 228.899 | 50.011
2025-10-22 11:08 | 71478.875 | 80919.484 | -39111.086 | 0.88 | 0.88333 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 25624.504 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 227.108 | 227.54 | 228.986 | 50.015
2025-10-22 11:09 | 60689.613 | 68781.563 | -33716.453 | 0.87 | 0.88235 | 21578.529 | 18881.213 | 20229.871 | 24275.846 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 227.216 | 227.972 | 229.309 | 50.022
2025-10-22 11:10 | 57992.297 | 67432.906 | -35065.109 | 0.85 | 0.86 | 20229.871 | 17532.555 | 18881.213 | 24275.846 | 21578.529 | 21578.529 | -12137.923 | -12137.923 | -9440.606 | 227.95 | 228.489 | 229.655 | 50.034
2025-10-22 11:11 | 60689.613 | 72827.539 | -37762.426 | 0.84 | 0.83333 | 22927.188 | 17532.555 | 20229.871 | 26973.162 | 22927.188 | 22927.188 | -14835.239 | -13486.581 | -9440.606 | 227.432 | 227.972 | 229.115 | 50.031
2025-10-22 11:12 | 63386.93 | 72827.539 | -36413.77 | 0.86 | 0.87037 | 22927.188 | 18881.213 | 21578.529 | 26973.162 | 22927.188 | 22927.188 | -13486.581 | -13486.581 | -10789.265 | 227.583 | 228.468 | 229.439 | 50.032
2025-10-22 11:13 | 72827.539 | 82268.141 | -37762.426 | 0.89 | 0.88525 | 25624.504 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 227.13 | 228.338 | 229.504 | 50.023
2025-10-22 11:14 | 72827.539 | 84965.461 | -40459.742 | 0.87 | 0.85714 | 25624.504 | 22927.188 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 226.569 | 227.324 | 228.727 | 50.022
2025-10-22 11:15 | 75524.852 | 87662.773 | -43157.059 | 0.86 | 0.86154 | 26973.162 | 22927.188 | 25624.504 | 31019.137 | 26973.162 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 226.332 | 227.281 | 228.662 | 50.027
2025-10-22 11:16 | 78222.172 | 90360.094 | -43157.059 | 0.87 | 0.86567 | 28321.82 | 24275.846 | 26973.162 | 33716.453 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 226.353 | 226.72 | 228.144 | 50.023
2025-10-22 11:17 | 78222.172 | 89011.43 | -41808.402 | 0.88 | 0.87879 | 28321.82 | 22927.188 | 26973.162 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -10789.265 | 226.957 | 227.259 | 228.856 | 50.018
2025-10-22 11:18 | 82268.141 | 94406.063 | -44505.715 | 0.87 | 0.87143 | 29670.479 | 24275.846 | 28321.82 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 226.828 | 227.389 | 229.137 | 50.014
2025-10-22 11:19 | 79570.828 | 90360.094 | -43157.059 | 0.88 | 0.8806 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 28321.82 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 225.878 | 226.914 | 228.382 | 50.008
2025-10-22 11:20 | 75524.852 | 87662.773 | -43157.059 | 0.86 | 0.86154 | 26973.162 | 22927.188 | 25624.504 | 31019.137 | 26973.162 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 225.814 | 226.742 | 228.274 | 50.004
2025-10-22 11:21 | 71478.875 | 83616.805 | -40459.742 | 0.87 | 0.85484 | 25624.504 | 21578.529 | 24275.846 | 29670.479 | 25624.504 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 226.267 | 227.087 | 228.77 | 50.015
2025-10-22 11:22 | 66084.242 | 78222.172 | -40459.742 | 0.85 | 0.84483 | 24275.846 | 20229.871 | 21578.529 | 28321.82 | 24275.846 | 24275.846 | -14835.239 | -14835.239 | -10789.265 | 226.418 | 227.065 | 228.856 | 50.023
2025-10-22 11:23 | 60689.613 | 71478.875 | -39111.086 | 0.84 | 0.84906 | 22927.188 | 17532.555 | 20229.871 | 26973.162 | 22927.188 | 22927.188 | -14835.239 | -13486.581 | -10789.265 | 226.914 | 227.518 | 229.18 | 50.022
2025-10-22 11:24 | 66084.242 | 76873.508 | -37762.426 | 0.87 | 0.85965 | 24275.846 | 20229.871 | 21578.529 | 28321.82 | 24275.846 | 24275.846 | -13486.581 | -13486.581 | -9440.606 | 226.418 | 226.526 | 228.856 | 49.996
2025-10-22 11:25 | 79570.828 | 90360.094 | -43157.059 | 0.87 | 0.8806 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -10789.265 | 226.137 | 225.814 | 228.899 | 49.997
2025-10-22 11:26 | 78222.172 | 89011.43 | -43157.059 | 0.87 | 0.87879 | 26973.162 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -10789.265 | 226.72 | 226.698 | 229.827 | 49.983
2025-10-22 11:27 | 76873.508 | 89011.43 | -44505.715 | 0.86 | 0.86364 | 26973.162 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 229.827 | 229.892 | 232.741 | 50.012
2025-10-22 11:28 | 74176.195 | 86314.117 | -44505.715 | 0.85 | 0.85938 | 25624.504 | 24275.846 | 24275.846 | 31019.137 | 29670.479 | 25624.504 | -16183.896 | -17532.555 | -10789.265 | 230.259 | 229.957 | 232.913 | 50.019
2025-10-22 11:29 | 72827.539 | 87662.773 | -47203.031 | 0.84 | 0.83077 | 25624.504 | 24275.846 | 22927.188 | 29670.479 | 31019.137 | 25624.504 | -16183.896 | -18881.213 | -12137.923 | 229.676 | 229.353 | 232.503 | 49.995
2025-10-22 11:30 | 68781.563 | 79570.828 | -40459.742 | 0.86 | 0.86441 | 22927.188 | 24275.846 | 21578.529 | 26973.162 | 28321.82 | 24275.846 | -13486.581 | -14835.239 | -10789.265 | 229.978 | 229.698 | 232.417 | 50.014
2025-10-22 11:31 | 70130.219 | 80919.484 | -40459.742 | 0.87 | 0.86667 | 22927.188 | 24275.846 | 22927.188 | 26973.162 | 28321.82 | 25624.504 | -13486.581 | -14835.239 | -12137.923 | 230.022 | 230.022 | 232.244 | 50.009
2025-10-22 11:32 | 74176.195 | 86314.117 | -44505.715 | 0.85 | 0.85938 | 25624.504 | 24275.846 | 24275.846 | 31019.137 | 29670.479 | 26973.162 | -16183.896 | -17532.555 | -12137.923 | 227.238 | 228.144 | 229.763 | 49.998
2025-10-22 11:33 | 75524.852 | 87662.773 | -43157.059 | 0.87 | 0.86154 | 26973.162 | 25624.504 | 24275.846 | 31019.137 | 29670.479 | 26973.162 | -14835.239 | -16183.896 | -12137.923 | 225.274 | 226.159 | 227.691 | 50.028
2025-10-22 11:34 | 75524.852 | 87662.773 | -43157.059 | 0.86 | 0.86154 | 26973.162 | 24275.846 | 24275.846 | 31019.137 | 29670.479 | 26973.162 | -14835.239 | -16183.896 | -12137.923 | 223.785 | 224.799 | 226.31 | 50.025
2025-10-22 11:35 | 72827.539 | 83616.805 | -41808.402 | 0.86 | 0.87097 | 25624.504 | 21578.529 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -12137.923 | 225.641 | 226.439 | 227.777 | 50.032
2025-10-22 11:36 | 74176.195 | 86314.117 | -41808.402 | 0.87 | 0.85938 | 26973.162 | 22927.188 | 24275.846 | 31019.137 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 224.174 | 225.145 | 226.59 | 50.026
2025-10-22 11:37 | 72827.539 | 83616.805 | -39111.086 | 0.88 | 0.87097 | 26973.162 | 22927.188 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 223.483 | 224.54 | 226.159 | 50.015
2025-10-22 11:38 | 76873.508 | 87662.773 | -43157.059 | 0.87 | 0.87692 | 26973.162 | 22927.188 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 224.26 | 225.339 | 226.828 | 50.005
2025-10-22 11:39 | 78222.172 | 89011.43 | -41808.402 | 0.88 | 0.87879 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 225.447 | 226.871 | 227.993 | 50.008
2025-10-22 11:40 | 71478.875 | 83616.805 | -41808.402 | 0.86 | 0.85484 | 25624.504 | 22927.188 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -12137.923 | 226.224 | 228.036 | 229.029 | 50.003
2025-10-22 11:41 | 76873.508 | 87662.773 | -41808.402 | 0.87 | 0.87692 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 226.008 | 227.972 | 228.964 | 50.007
2025-10-22 11:42 | 74176.195 | 84965.461 | -40459.742 | 0.87 | 0.87302 | 26973.162 | 22927.188 | 24275.846 | 31019.137 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 225.619 | 227.562 | 228.641 | 50.015
2025-10-22 11:43 | 78222.172 | 89011.43 | -41808.402 | 0.88 | 0.87879 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 225.663 | 227.108 | 228.489 | 50.016
2025-10-22 11:44 | 76873.508 | 87662.773 | -41808.402 | 0.88 | 0.87692 | 26973.162 | 22927.188 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -10789.265 | 225.792 | 226.763 | 228.36 | 50.008
2025-10-22 11:45 | 76873.508 | 87662.773 | -41808.402 | 0.88 | 0.87692 | 28321.82 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -10789.265 | 224.95 | 225.9 | 227.713 | 50.002
2025-10-22 11:46 | 75524.852 | 86314.117 | -41808.402 | 0.87 | 0.875 | 26973.162 | 22927.188 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 225.274 | 226.569 | 228.166 | 50.011
2025-10-22 11:47 | 72827.539 | 83616.805 | -41808.402 | 0.86 | 0.87097 | 25624.504 | 22927.188 | 24275.846 | 29670.479 | 28321.82 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 225.9 | 226.914 | 228.511 | 49.991
2025-10-22 11:48 | 72827.539 | 83616.805 | -40459.742 | 0.87 | 0.87097 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 28321.82 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 224.821 | 225.986 | 227.669 | 49.998
2025-10-22 11:49 | 75524.852 | 86314.117 | -41808.402 | 0.87 | 0.875 | 26973.162 | 24275.846 | 24275.846 | 31019.137 | 28321.82 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 224.821 | 225.857 | 227.669 | 50.001
2025-10-22 11:50 | 75524.852 | 86314.117 | -41808.402 | 0.87 | 0.875 | 26973.162 | 24275.846 | 24275.846 | 31019.137 | 28321.82 | 26973.162 | -16183.896 | -14835.239 | -10789.265 | 224.95 | 225.425 | 227.605 | 49.993
2025-10-22 11:51 | 79570.828 | 91708.75 | -43157.059 | 0.88 | 0.86765 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 225.317 | 226.742 | 228.36 | 50.013
2025-10-22 11:52 | 79570.828 | 90360.094 | -43157.059 | 0.87 | 0.8806 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 225.102 | 226.936 | 228.489 | 50.019
2025-10-22 11:53 | 74176.195 | 86314.117 | -43157.059 | 0.86 | 0.85938 | 25624.504 | 24275.846 | 24275.846 | 31019.137 | 28321.82 | 26973.162 | -16183.896 | -16183.896 | -10789.265 | 225.08 | 226.439 | 228.489 | 50.011
2025-10-22 11:54 | 78222.172 | 90360.094 | -44505.715 | 0.87 | 0.86567 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 224.238 | 225.555 | 227.475 | 50.01
2025-10-22 11:55 | 84965.461 | 97103.383 | -47203.031 | 0.87 | 0.875 | 29670.479 | 25624.504 | 28321.82 | 35065.109 | 31019.137 | 31019.137 | -17532.555 | -16183.896 | -13486.581 | 224.325 | 225.77 | 227.281 | 50.011
2025-10-22 11:56 | 79570.828 | 90360.094 | -43157.059 | 0.87 | 0.8806 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 28321.82 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 224.368 | 225.576 | 227.195 | 50.013
2025-10-22 11:57 | 76873.508 | 87662.773 | -41808.402 | 0.87 | 0.87692 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 224.994 | 226.375 | 227.972 | 50.019
2025-10-22 11:58 | 76873.508 | 89011.43 | -43157.059 | 0.87 | 0.86364 | 28321.82 | 22927.188 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 224.497 | 225.533 | 227.173 | 50.025
2025-10-22 11:59 | 72827.539 | 84965.461 | -41808.402 | 0.86 | 0.85714 | 25624.504 | 22927.188 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -12137.923 | 225.274 | 226.849 | 227.907 | 50.024
2025-10-22 12:00 | 72827.539 | 82268.141 | -39111.086 | 0.88 | 0.88525 | 24275.846 | 24275.846 | 22927.188 | 28321.82 | 28321.82 | 25624.504 | -13486.581 | -14835.239 | -12137.923 | 225.015 | 226.439 | 227.993 | 50.016
2025-10-22 12:01 | 72827.539 | 82268.141 | -39111.086 | 0.88 | 0.88525 | 24275.846 | 25624.504 | 22927.188 | 28321.82 | 28321.82 | 25624.504 | -13486.581 | -14835.239 | -10789.265 | 224.907 | 225.814 | 227.95 | 50.021
2025-10-22 12:02 | 75524.852 | 86314.117 | -40459.742 | 0.88 | 0.875 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -13486.581 | -14835.239 | -12137.923 | 224.692 | 225.922 | 228.123 | 49.996
2025-10-22 12:03 | 76873.508 | 87662.773 | -40459.742 | 0.88 | 0.87692 | 25624.504 | 26973.162 | 24275.846 | 29670.479 | 31019.137 | 26973.162 | -13486.581 | -14835.239 | -12137.923 | 224.692 | 225.706 | 227.713 | 49.998
2025-10-22 12:04 | 75524.852 | 84965.461 | -40459.742 | 0.88 | 0.88889 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -13486.581 | -14835.239 | -12137.923 | 224.454 | 225.49 | 227.281 | 50.002
2025-10-22 12:05 | 72827.539 | 82268.141 | -37762.426 | 0.89 | 0.88525 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 223.893 | 224.217 | 226.698 | 49.99
2025-10-22 12:06 | 71478.875 | 80919.484 | -37762.426 | 0.88 | 0.88333 | 24275.846 | 22927.188 | 22927.188 | 28321.82 | 26973.162 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 223.872 | 224.346 | 226.439 | 50.012
2025-10-22 12:07 | 68781.563 | 78222.172 | -36413.77 | 0.88 | 0.87931 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 224.023 | 224.972 | 226.31 | 50.013
2025-10-22 12:08 | 67432.906 | 76873.508 | -36413.77 | 0.88 | 0.87719 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 25624.504 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 225.058 | 226.245 | 227.216 | 49.992
2025-10-22 12:09 | 71478.875 | 82268.141 | -39111.086 | 0.88 | 0.86885 | 25624.504 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 225.727 | 226.828 | 228.23 | 50.008
2025-10-22 12:10 | 76873.508 | 86314.117 | -39111.086 | 0.89 | 0.89062 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 29670.479 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 224.54 | 225.339 | 227.41 | 50.027
2025-10-22 12:11 | 74176.195 | 82268.141 | -37762.426 | 0.89 | 0.90164 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 224.044 | 224.411 | 226.655 | 50.018
2025-10-22 12:12 | 74176.195 | 83616.805 | -39111.086 | 0.88 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 224.648 | 225.015 | 227.389 | 50.027
2025-10-22 12:13 | 71478.875 | 80919.484 | -37762.426 | 0.88 | 0.88333 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 224.476 | 224.713 | 227.044 | 50.024
2025-10-22 12:14 | 72827.539 | 82268.141 | -37762.426 | 0.88 | 0.88525 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 224.023 | 224.497 | 226.569 | 50.026
2025-10-22 12:15 | 74176.195 | 83616.805 | -39111.086 | 0.88 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -14835.239 | -13486.581 | -10789.265 | 224.303 | 224.713 | 226.936 | 50.021
2025-10-22 12:16 | 76873.508 | 89011.43 | -43157.059 | 0.87 | 0.86364 | 26973.162 | 24275.846 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -16183.896 | -10789.265 | 223.936 | 224.433 | 226.526 | 50.001
2025-10-22 12:17 | 70130.219 | 82268.141 | -41808.402 | 0.85 | 0.85246 | 25624.504 | 21578.529 | 22927.188 | 29670.479 | 26973.162 | 25624.504 | -14835.239 | -16183.896 | -12137.923 | 224.087 | 225.49 | 226.612 | 49.998
2025-10-22 12:18 | 74176.195 | 86314.117 | -43157.059 | 0.86 | 0.85938 | 26973.162 | 22927.188 | 24275.846 | 31019.137 | 28321.82 | 26973.162 | -14835.239 | -16183.896 | -12137.923 | 223.764 | 225.36 | 226.288 | 50
2025-10-22 12:19 | 74176.195 | 83616.805 | -39111.086 | 0.88 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 223.699 | 225.77 | 226.332 | 50.008
2025-10-22 12:20 | 72827.539 | 82268.141 | -37762.426 | 0.89 | 0.88525 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 223.224 | 224.605 | 225.49 | 50.008
2025-10-22 12:21 | 70130.219 | 79570.828 | -37762.426 | 0.88 | 0.88136 | 24275.846 | 21578.529 | 22927.188 | 28321.82 | 25624.504 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 224.584 | 225.468 | 227.108 | 50.007
2025-10-22 12:22 | 70130.219 | 78222.172 | -36413.77 | 0.89 | 0.89655 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 224.476 | 225.663 | 227.259 | 50.018
2025-10-22 12:23 | 72827.539 | 82268.141 | -37762.426 | 0.88 | 0.88525 | 25624.504 | 22927.188 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 223.764 | 224.433 | 226.59 | 50.023
2025-10-22 12:24 | 76873.508 | 87662.773 | -41808.402 | 0.87 | 0.87692 | 28321.82 | 22927.188 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -10789.265 | 223.613 | 224.476 | 226.547 | 50.018
2025-10-22 12:25 | 79570.828 | 91708.75 | -44505.715 | 0.87 | 0.86765 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 223.979 | 224.907 | 226.936 | 50.011
2025-10-22 12:26 | 74176.195 | 86314.117 | -43157.059 | 0.86 | 0.85938 | 26973.162 | 22927.188 | 24275.846 | 31019.137 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -12137.923 | 223.569 | 224.778 | 226.72 | 50.01
2025-10-22 12:27 | 72827.539 | 83616.805 | -41808.402 | 0.86 | 0.87097 | 25624.504 | 21578.529 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 223.915 | 224.713 | 226.655 | 49.999
2025-10-22 12:28 | 72827.539 | 82268.141 | -36413.77 | 0.89 | 0.88525 | 25624.504 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -12137.923 | -10789.265 | 224.389 | 225.253 | 226.957 | 50.009
2025-10-22 12:29 | 76873.508 | 84965.461 | -37762.426 | 0.89 | 0.90476 | 26973.162 | 24275.846 | 25624.504 | 29670.479 | 26973.162 | 28321.82 | -13486.581 | -13486.581 | -12137.923 | 223.656 | 224.95 | 226.159 | 50.02
2025-10-22 12:30 | 74176.195 | 83616.805 | -37762.426 | 0.89 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 224.195 | 225.878 | 226.569 | 50.027
2025-10-22 12:31 | 75524.852 | 83616.805 | -37762.426 | 0.89 | 0.90323 | 25624.504 | 24275.846 | 25624.504 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 224.562 | 226.504 | 227.173 | 50.018
2025-10-22 12:32 | 74176.195 | 83616.805 | -40459.742 | 0.88 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -14835.239 | -12137.923 | 224.001 | 225.317 | 226.871 | 49.993
2025-10-22 12:33 | 74176.195 | 84965.461 | -40459.742 | 0.88 | 0.87302 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -14835.239 | -14835.239 | -12137.923 | 224.152 | 225.209 | 227.152 | 49.989
2025-10-22 12:34 | 75524.852 | 83616.805 | -36413.77 | 0.9 | 0.90323 | 24275.846 | 26973.162 | 24275.846 | 26973.162 | 29670.479 | 26973.162 | -12137.923 | -13486.581 | -10789.265 | 223.656 | 224.087 | 226.504 | 49.994
2025-10-22 12:35 | 71478.875 | 79570.828 | -35065.109 | 0.9 | 0.89831 | 22927.188 | 25624.504 | 22927.188 | 25624.504 | 29670.479 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 224.692 | 225.188 | 227.518 | 49.993
2025-10-22 12:36 | 78222.172 | 89011.43 | -40459.742 | 0.89 | 0.87879 | 25624.504 | 26973.162 | 25624.504 | 29670.479 | 31019.137 | 26973.162 | -13486.581 | -14835.239 | -10789.265 | 224.13 | 224.584 | 227.087 | 49.988
2025-10-22 12:37 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 28321.82 | 28321.82 | 26973.162 | 32367.793 | 33716.453 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 223.915 | 224.778 | 227.259 | 49.988
2025-10-22 12:38 | 78222.172 | 90360.094 | -44505.715 | 0.87 | 0.86567 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 223.72 | 224.756 | 226.806 | 50
2025-10-22 12:39 | 79570.828 | 91708.75 | -44505.715 | 0.87 | 0.86765 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 223.505 | 224.67 | 226.569 | 50.007
2025-10-22 12:40 | 84965.461 | 97103.383 | -47203.031 | 0.87 | 0.875 | 29670.479 | 26973.162 | 26973.162 | 33716.453 | 32367.793 | 31019.137 | -16183.896 | -17532.555 | -13486.581 | 223.462 | 224.994 | 226.569 | 50.016
2025-10-22 12:41 | 83616.805 | 95754.727 | -45854.375 | 0.88 | 0.87324 | 29670.479 | 25624.504 | 28321.82 | 33716.453 | 31019.137 | 31019.137 | -16183.896 | -16183.896 | -13486.581 | 224.13 | 225.663 | 227.065 | 50.01
2025-10-22 12:42 | 83616.805 | 94406.063 | -44505.715 | 0.88 | 0.88571 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 31019.137 | -16183.896 | -16183.896 | -12137.923 | 224.152 | 225.274 | 226.849 | 50.011
2025-10-22 12:43 | 82268.141 | 94406.063 | -44505.715 | 0.88 | 0.87143 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.13 | 225.425 | 226.893 | 50.025
2025-10-22 12:44 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 224.152 | 225.598 | 226.849 | 50.031
2025-10-22 12:45 | 79570.828 | 90360.094 | -43157.059 | 0.87 | 0.8806 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -14835.239 | -16183.896 | -12137.923 | 223.915 | 225.663 | 226.677 | 50.02
2025-10-22 12:46 | 84965.461 | 97103.383 | -45854.375 | 0.88 | 0.875 | 29670.479 | 26973.162 | 28321.82 | 33716.453 | 31019.137 | 31019.137 | -16183.896 | -16183.896 | -13486.581 | 224.389 | 226.31 | 227.497 | 50.021
2025-10-22 12:47 | 86314.117 | 98452.039 | -47203.031 | 0.87 | 0.87671 | 31019.137 | 26973.162 | 28321.82 | 35065.109 | 31019.137 | 31019.137 | -17532.555 | -16183.896 | -13486.581 | 223.699 | 225.253 | 226.504 | 50.02
2025-10-22 12:48 | 86314.117 | 98452.039 | -47203.031 | 0.87 | 0.87671 | 31019.137 | 26973.162 | 28321.82 | 35065.109 | 32367.793 | 31019.137 | -17532.555 | -16183.896 | -13486.581 | 224.411 | 225.835 | 227.41 | 50.024
2025-10-22 12:49 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 224.54 | 225.857 | 227.583 | 50.027
2025-10-22 12:50 | 80919.484 | 94406.063 | -45854.375 | 0.87 | 0.85714 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.26 | 225.339 | 227.195 | 50.006
2025-10-22 12:51 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 31019.137 | -16183.896 | -16183.896 | -12137.923 | 223.677 | 224.756 | 226.698 | 50.013
2025-10-22 12:52 | 84965.461 | 97103.383 | -45854.375 | 0.88 | 0.875 | 29670.479 | 26973.162 | 28321.82 | 33716.453 | 31019.137 | 31019.137 | -16183.896 | -16183.896 | -13486.581 | 223.764 | 225.339 | 227.152 | 50.018
2025-10-22 12:53 | 83616.805 | 95754.727 | -45854.375 | 0.87 | 0.87324 | 29670.479 | 26973.162 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 223.634 | 225.49 | 226.72 | 50.035
2025-10-22 12:54 | 83616.805 | 95754.727 | -44505.715 | 0.88 | 0.87324 | 29670.479 | 26973.162 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 223.44 | 225.404 | 226.137 | 50.019
2025-10-22 12:55 | 82268.141 | 94406.063 | -44505.715 | 0.87 | 0.87143 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -13486.581 | 224.692 | 226.504 | 227.562 | 50.018
2025-10-22 12:56 | 86314.117 | 98452.039 | -47203.031 | 0.88 | 0.87671 | 31019.137 | 26973.162 | 28321.82 | 35065.109 | 32367.793 | 31019.137 | -16183.896 | -16183.896 | -13486.581 | 224.627 | 226.18 | 227.346 | 50.011
2025-10-22 12:57 | 79570.828 | 91708.75 | -45854.375 | 0.87 | 0.86765 | 28321.82 | 26973.162 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -17532.555 | -12137.923 | 224.497 | 226.375 | 227.389 | 50.015
2025-10-22 12:58 | 86314.117 | 98452.039 | -47203.031 | 0.87 | 0.87671 | 29670.479 | 28321.82 | 28321.82 | 33716.453 | 33716.453 | 31019.137 | -16183.896 | -17532.555 | -13486.581 | 225.253 | 226.979 | 228.382 | 50.031
2025-10-22 12:59 | 86314.117 | 97103.383 | -45854.375 | 0.88 | 0.88889 | 29670.479 | 28321.82 | 28321.82 | 33716.453 | 32367.793 | 31019.137 | -16183.896 | -17532.555 | -13486.581 | 225.188 | 226.634 | 228.468 | 50.034
2025-10-22 13:00 | 84965.461 | 95754.727 | -44505.715 | 0.88 | 0.88732 | 29670.479 | 26973.162 | 26973.162 | 33716.453 | 32367.793 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.692 | 225.878 | 227.734 | 50.031
2025-10-22 13:01 | 86314.117 | 98452.039 | -45854.375 | 0.88 | 0.87671 | 29670.479 | 29670.479 | 26973.162 | 33716.453 | 33716.453 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 224.454 | 225.447 | 227.799 | 50.021
2025-10-22 13:02 | 86314.117 | 99800.695 | -48551.691 | 0.87 | 0.86486 | 29670.479 | 29670.479 | 26973.162 | 33716.453 | 35065.109 | 31019.137 | -17532.555 | -18881.213 | -13486.581 | 225.749 | 226.569 | 228.943 | 50.003
2025-10-22 13:03 | 83616.805 | 95754.727 | -45854.375 | 0.87 | 0.87324 | 28321.82 | 28321.82 | 25624.504 | 32367.793 | 33716.453 | 28321.82 | -16183.896 | -17532.555 | -12137.923 | 225.123 | 225.792 | 228.101 | 49.996
2025-10-22 13:04 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 28321.82 | 28321.82 | 26973.162 | 32367.793 | 32367.793 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 224.605 | 225.253 | 227.799 | 50.005
2025-10-22 13:05 | 86314.117 | 98452.039 | -47203.031 | 0.87 | 0.87671 | 29670.479 | 28321.82 | 28321.82 | 35065.109 | 32367.793 | 31019.137 | -17532.555 | -17532.555 | -12137.923 | 224.756 | 225.317 | 228.209 | 50.006
2025-10-22 13:06 | 84965.461 | 97103.383 | -47203.031 | 0.87 | 0.875 | 29670.479 | 26973.162 | 28321.82 | 33716.453 | 32367.793 | 31019.137 | -17532.555 | -17532.555 | -12137.923 | 224.994 | 225.749 | 228.317 | 50.016
2025-10-22 13:07 | 79570.828 | 91708.75 | -43157.059 | 0.87 | 0.86765 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 28321.82 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.907 | 225.835 | 227.799 | 50.015
2025-10-22 13:08 | 80919.484 | 91708.75 | -43157.059 | 0.88 | 0.88235 | 29670.479 | 24275.846 | 26973.162 | 33716.453 | 28321.82 | 29670.479 | -16183.896 | -14835.239 | -10789.265 | 225.727 | 226.396 | 228.641 | 50.022
2025-10-22 13:09 | 78222.172 | 90360.094 | -44505.715 | 0.87 | 0.86567 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 28321.82 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 225.619 | 226.439 | 228.597 | 50.027
2025-10-22 13:10 | 79570.828 | 91708.75 | -43157.059 | 0.87 | 0.86765 | 28321.82 | 24275.846 | 26973.162 | 33716.453 | 28321.82 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 225.253 | 225.9 | 228.036 | 50.02
2025-10-22 13:11 | 83616.805 | 94406.063 | -44505.715 | 0.88 | 0.88571 | 29670.479 | 25624.504 | 28321.82 | 33716.453 | 29670.479 | 31019.137 | -16183.896 | -16183.896 | -12137.923 | 225.533 | 226.677 | 228.576 | 50.024
2025-10-22 13:12 | 82268.141 | 94406.063 | -44505.715 | 0.88 | 0.87143 | 29670.479 | 25624.504 | 28321.82 | 33716.453 | 29670.479 | 31019.137 | -16183.896 | -16183.896 | -12137.923 | 226.094 | 227.648 | 229.309 | 50.016
2025-10-22 13:13 | 82268.141 | 93057.406 | -43157.059 | 0.88 | 0.88406 | 29670.479 | 25624.504 | 28321.82 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 225.555 | 226.72 | 228.77 | 50.014
2025-10-22 13:14 | 80919.484 | 91708.75 | -43157.059 | 0.88 | 0.88235 | 29670.479 | 24275.846 | 26973.162 | 33716.453 | 28321.82 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 225.382 | 226.051 | 228.382 | 50.009
2025-10-22 13:15 | 82268.141 | 94406.063 | -44505.715 | 0.88 | 0.87143 | 29670.479 | 25624.504 | 28321.82 | 33716.453 | 29670.479 | 31019.137 | -16183.896 | -16183.896 | -12137.923 | 225.663 | 226.72 | 228.856 | 50.011
2025-10-22 13:16 | 76873.508 | 89011.43 | -43157.059 | 0.87 | 0.86364 | 28321.82 | 22927.188 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 225.382 | 226.31 | 228.446 | 49.998
2025-10-22 13:17 | 70130.219 | 80919.484 | -39111.086 | 0.87 | 0.86667 | 25624.504 | 20229.871 | 24275.846 | 29670.479 | 25624.504 | 25624.504 | -14835.239 | -13486.581 | -9440.606 | 224.692 | 224.843 | 227.044 | 49.986
2025-10-22 13:18 | 80919.484 | 91708.75 | -44505.715 | 0.87 | 0.88235 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.619 | 226.094 | 228.209 | 49.983
2025-10-22 13:19 | 76873.508 | 87662.773 | -41808.402 | 0.87 | 0.87692 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 26973.162 | -16183.896 | -14835.239 | -10789.265 | 225.36 | 225.619 | 228.144 | 49.985
2025-10-22 13:20 | 78222.172 | 89011.43 | -41808.402 | 0.87 | 0.87879 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 29670.479 | 28321.82 | -16183.896 | -16183.896 | -10789.265 | 225.425 | 226.116 | 227.993 | 49.992
2025-10-22 13:21 | 79570.828 | 91708.75 | -43157.059 | 0.88 | 0.86765 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 225.986 | 226.763 | 228.425 | 50.01
2025-10-22 13:22 | 79570.828 | 91708.75 | -43157.059 | 0.87 | 0.86765 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 225.727 | 226.677 | 228.468 | 50.001
2025-10-22 13:23 | 75524.852 | 87662.773 | -43157.059 | 0.87 | 0.86154 | 26973.162 | 24275.846 | 24275.846 | 31019.137 | 28321.82 | 26973.162 | -16183.896 | -16183.896 | -10789.265 | 225.576 | 225.792 | 227.885 | 49.995
2025-10-22 13:24 | 72827.539 | 84965.461 | -41808.402 | 0.86 | 0.85714 | 25624.504 | 22927.188 | 22927.188 | 31019.137 | 28321.82 | 25624.504 | -16183.896 | -16183.896 | -10789.265 | 226.806 | 227.044 | 229.029 | 49.992
2025-10-22 13:25 | 74176.195 | 86314.117 | -41808.402 | 0.87 | 0.85938 | 26973.162 | 22927.188 | 24275.846 | 31019.137 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 225.684 | 226.18 | 227.972 | 50.011
2025-10-22 13:26 | 72827.539 | 83616.805 | -41808.402 | 0.86 | 0.87097 | 25624.504 | 21578.529 | 24275.846 | 31019.137 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 225.468 | 226.159 | 227.691 | 50.015
2025-10-22 13:27 | 75524.852 | 84965.461 | -40459.742 | 0.88 | 0.88889 | 25624.504 | 24275.846 | 25624.504 | 29670.479 | 26973.162 | 28321.82 | -14835.239 | -13486.581 | -12137.923 | 226.806 | 227.454 | 228.921 | 50.012
2025-10-22 13:28 | 72827.539 | 82268.141 | -37762.426 | 0.89 | 0.88525 | 25624.504 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 226.245 | 227.152 | 228.403 | 50.011
2025-10-22 13:29 | 70130.219 | 80919.484 | -37762.426 | 0.88 | 0.86667 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 25624.504 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 226.439 | 227.626 | 229.072 | 50.004
2025-10-22 13:30 | 70130.219 | 79570.828 | -37762.426 | 0.88 | 0.88136 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 227.691 | 228.899 | 230.432 | 50.005
2025-10-22 13:31 | 71478.875 | 80919.484 | -37762.426 | 0.88 | 0.88333 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 28321.82 | 25624.504 | -13486.581 | -14835.239 | -10789.265 | 226.569 | 227.497 | 228.943 | 49.976
2025-10-22 13:32 | 74176.195 | 83616.805 | -40459.742 | 0.88 | 0.8871 | 24275.846 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -13486.581 | -14835.239 | -12137.923 | 227.216 | 228.317 | 230.151 | 49.958
2025-10-22 13:33 | 72827.539 | 83616.805 | -40459.742 | 0.88 | 0.87097 | 24275.846 | 25624.504 | 22927.188 | 28321.82 | 29670.479 | 25624.504 | -13486.581 | -14835.239 | -12137.923 | 227.173 | 228.748 | 230.41 | 49.971
2025-10-22 13:34 | 72827.539 | 83616.805 | -40459.742 | 0.88 | 0.87097 | 24275.846 | 25624.504 | 22927.188 | 28321.82 | 29670.479 | 25624.504 | -13486.581 | -14835.239 | -12137.923 | 227.022 | 228.533 | 230.151 | 49.985
2025-10-22 13:35 | 80919.484 | 93057.406 | -45854.375 | 0.87 | 0.86957 | 28321.82 | 26973.162 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -17532.555 | -12137.923 | 227.108 | 228.123 | 230.345 | 49.992
2025-10-22 13:36 | 79570.828 | 91708.75 | -45854.375 | 0.86 | 0.86765 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -17532.555 | -12137.923 | 228.23 | 229.029 | 231.424 | 49.996
2025-10-22 13:37 | 71478.875 | 83616.805 | -41808.402 | 0.86 | 0.85484 | 25624.504 | 21578.529 | 22927.188 | 29670.479 | 26973.162 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 228.23 | 229.223 | 231.295 | 50.004
2025-10-22 13:38 | 70130.219 | 83616.805 | -43157.059 | 0.85 | 0.83871 | 25624.504 | 21578.529 | 22927.188 | 29670.479 | 26973.162 | 25624.504 | -16183.896 | -16183.896 | -12137.923 | 227.605 | 228.792 | 230.798 | 49.996
2025-10-22 13:39 | 67432.906 | 79570.828 | -41808.402 | 0.84 | 0.84746 | 24275.846 | 20229.871 | 22927.188 | 29670.479 | 25624.504 | 25624.504 | -16183.896 | -14835.239 | -12137.923 | 227.777 | 228.899 | 230.928 | 49.992
2025-10-22 13:40 | 66084.242 | 76873.508 | -39111.086 | 0.86 | 0.85965 | 22927.188 | 21578.529 | 21578.529 | 26973.162 | 24275.846 | 24275.846 | -13486.581 | -13486.581 | -12137.923 | 228.705 | 230 | 231.77 | 49.992
2025-10-22 13:41 | 66084.242 | 74176.195 | -35065.109 | 0.88 | 0.89091 | 21578.529 | 21578.529 | 21578.529 | 24275.846 | 24275.846 | 24275.846 | -12137.923 | -10789.265 | -10789.265 | 226.763 | 227.864 | 229.784 | 50
2025-10-22 13:42 | 66084.242 | 74176.195 | -35065.109 | 0.89 | 0.89091 | 21578.529 | 21578.529 | 21578.529 | 24275.846 | 24275.846 | 24275.846 | -12137.923 | -10789.265 | -10789.265 | 228.576 | 229.547 | 231.511 | 50.003
2025-10-22 13:43 | 67432.906 | 75524.852 | -33716.453 | 0.89 | 0.89286 | 21578.529 | 22927.188 | 22927.188 | 24275.846 | 25624.504 | 24275.846 | -12137.923 | -10789.265 | -10789.265 | 228.899 | 229.461 | 231.532 | 50.008
2025-10-22 13:44 | 70130.219 | 78222.172 | -35065.109 | 0.89 | 0.89655 | 22927.188 | 24275.846 | 22927.188 | 25624.504 | 26973.162 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 228.209 | 228.878 | 230.798 | 50
2025-10-22 13:45 | 75524.852 | 84965.461 | -39111.086 | 0.88 | 0.88889 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -14835.239 | -13486.581 | -12137.923 | 228.878 | 229.892 | 231.877 | 49.995
2025-10-22 13:46 | 70130.219 | 79570.828 | -36413.77 | 0.88 | 0.88136 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 228.446 | 229.353 | 231.273 | 50.004
2025-10-22 13:47 | 71478.875 | 80919.484 | -37762.426 | 0.88 | 0.88333 | 24275.846 | 22927.188 | 22927.188 | 28321.82 | 26973.162 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 229.072 | 229.439 | 231.683 | 49.999
2025-10-22 13:48 | 71478.875 | 82268.141 | -39111.086 | 0.88 | 0.86885 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 25624.504 | -14835.239 | -13486.581 | -10789.265 | 228.986 | 229.417 | 231.575 | 50.011
2025-10-22 13:49 | 72827.539 | 82268.141 | -39111.086 | 0.88 | 0.88525 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 228.36 | 229.288 | 230.949 | 50.012
2025-10-22 13:50 | 66084.242 | 74176.195 | -35065.109 | 0.88 | 0.89091 | 22927.188 | 20229.871 | 22927.188 | 26973.162 | 22927.188 | 24275.846 | -13486.581 | -12137.923 | -10789.265 | 226.893 | 227.605 | 229.115 | 50.018
2025-10-22 13:51 | 68781.563 | 78222.172 | -36413.77 | 0.88 | 0.87931 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 226.439 | 227.928 | 228.77 | 50.018
2025-10-22 13:52 | 67432.906 | 76873.508 | -36413.77 | 0.88 | 0.87719 | 22927.188 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 227.238 | 228.727 | 229.784 | 50.018
2025-10-22 13:53 | 71478.875 | 82268.141 | -39111.086 | 0.87 | 0.86885 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -14835.239 | -13486.581 | -12137.923 | 227.367 | 228.878 | 230.043 | 50.032
2025-10-22 13:54 | 67432.906 | 75524.852 | -32367.793 | 0.9 | 0.89286 | 22927.188 | 22927.188 | 22927.188 | 25624.504 | 25624.504 | 25624.504 | -10789.265 | -10789.265 | -10789.265 | 226.979 | 228.036 | 229.288 | 50.025
2025-10-22 13:55 | 67432.906 | 74176.195 | -32367.793 | 0.9 | 0.90909 | 21578.529 | 22927.188 | 22927.188 | 24275.846 | 24275.846 | 24275.846 | -10789.265 | -10789.265 | -10789.265 | 227.087 | 228.166 | 229.245 | 50.017
2025-10-22 13:56 | 74176.195 | 83616.805 | -37762.426 | 0.89 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 227.108 | 228.036 | 229.158 | 49.991
2025-10-22 13:57 | 74176.195 | 83616.805 | -39111.086 | 0.88 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 226.957 | 227.777 | 228.943 | 49.998
2025-10-22 13:58 | 72827.539 | 82268.141 | -37762.426 | 0.89 | 0.88525 | 25624.504 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 226.483 | 227.259 | 228.425 | 50.01
2025-10-22 13:59 | 75524.852 | 84965.461 | -40459.742 | 0.88 | 0.88889 | 25624.504 | 24275.846 | 25624.504 | 29670.479 | 28321.82 | 28321.82 | -13486.581 | -13486.581 | -12137.923 | 227.432 | 228.382 | 229.568 | 50.007
2025-10-22 14:00 | 71478.875 | 80919.484 | -39111.086 | 0.88 | 0.88333 | 24275.846 | 22927.188 | 22927.188 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 227.324 | 228.576 | 229.655 | 50.014
2025-10-22 14:01 | 75524.852 | 84965.461 | -39111.086 | 0.88 | 0.88889 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 226.439 | 227.346 | 228.77 | 50.011
2025-10-22 14:02 | 76873.508 | 87662.773 | -40459.742 | 0.88 | 0.87692 | 25624.504 | 25624.504 | 24275.846 | 29670.479 | 29670.479 | 26973.162 | -13486.581 | -14835.239 | -12137.923 | 227.022 | 227.583 | 229.633 | 50.013
2025-10-22 14:03 | 74176.195 | 83616.805 | -39111.086 | 0.88 | 0.8871 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -14835.239 | -10789.265 | 225.792 | 226.116 | 228.425 | 50.007
2025-10-22 14:04 | 75524.852 | 86314.117 | -39111.086 | 0.89 | 0.875 | 25624.504 | 25624.504 | 25624.504 | 29670.479 | 28321.82 | 26973.162 | -14835.239 | -13486.581 | -10789.265 | 225.339 | 225.037 | 227.799 | 50.013
2025-10-22 14:05 | 71478.875 | 80919.484 | -37762.426 | 0.88 | 0.88333 | 24275.846 | 24275.846 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 227.065 | 227.238 | 229.568 | 50.011
2025-10-22 14:06 | 75524.852 | 86314.117 | -40459.742 | 0.88 | 0.875 | 25624.504 | 25624.504 | 24275.846 | 29670.479 | 29670.479 | 26973.162 | -14835.239 | -14835.239 | -12137.923 | 226.483 | 226.72 | 228.986 | 50.001
2025-10-22 14:07 | 71478.875 | 80919.484 | -37762.426 | 0.88 | 0.88333 | 22927.188 | 25624.504 | 22927.188 | 26973.162 | 29670.479 | 24275.846 | -13486.581 | -14835.239 | -10789.265 | 226.073 | 226.677 | 228.619 | 50.002
2025-10-22 14:08 | 68781.563 | 78222.172 | -36413.77 | 0.88 | 0.87931 | 22927.188 | 22927.188 | 22927.188 | 26973.162 | 26973.162 | 24275.846 | -13486.581 | -13486.581 | -10789.265 | 227.13 | 227.885 | 229.353 | 50.003
2025-10-22 14:09 | 68781.563 | 78222.172 | -36413.77 | 0.89 | 0.87931 | 22927.188 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 24275.846 | -13486.581 | -12137.923 | -10789.265 | 227.108 | 227.41 | 229.504 | 50.003
2025-10-22 14:10 | 67432.906 | 76873.508 | -36413.77 | 0.88 | 0.87719 | 22927.188 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 24275.846 | -13486.581 | -13486.581 | -10789.265 | 225.922 | 226.332 | 228.576 | 49.984
2025-10-22 14:11 | 68781.563 | 76873.508 | -36413.77 | 0.88 | 0.89474 | 22927.188 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 24275.846 | -13486.581 | -12137.923 | -9440.606 | 225.835 | 225.619 | 228.533 | 49.991
2025-10-22 14:12 | 67432.906 | 76873.508 | -37762.426 | 0.87 | 0.87719 | 22927.188 | 22927.188 | 21578.529 | 26973.162 | 25624.504 | 24275.846 | -13486.581 | -13486.581 | -10789.265 | 226.073 | 226.353 | 228.705 | 50.008
2025-10-22 14:13 | 62038.273 | 71478.875 | -33716.453 | 0.87 | 0.86792 | 21578.529 | 20229.871 | 20229.871 | 24275.846 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 226.245 | 226.785 | 228.77 | 49.984
2025-10-22 14:14 | 60689.613 | 70130.219 | -33716.453 | 0.88 | 0.86538 | 21578.529 | 18881.213 | 20229.871 | 24275.846 | 22927.188 | 22927.188 | -12137.923 | -10789.265 | -9440.606 | 226.245 | 226.547 | 228.641 | 49.987
2025-10-22 14:15 | 62038.273 | 70130.219 | -31019.137 | 0.89 | 0.88462 | 20229.871 | 20229.871 | 20229.871 | 22927.188 | 22927.188 | 22927.188 | -10789.265 | -10789.265 | -10789.265 | 226.698 | 226.893 | 228.792 | 49.98
2025-10-22 14:16 | 59340.957 | 67432.906 | -29670.479 | 0.9 | 0.88 | 20229.871 | 20229.871 | 20229.871 | 22927.188 | 22927.188 | 21578.529 | -9440.606 | -9440.606 | -9440.606 | 226.051 | 226.677 | 227.972 | 49.986
2025-10-22 14:17 | 63386.93 | 71478.875 | -32367.793 | 0.9 | 0.88679 | 21578.529 | 21578.529 | 21578.529 | 24275.846 | 24275.846 | 24275.846 | -10789.265 | -10789.265 | -10789.265 | 225.447 | 226.72 | 227.713 | 49.991
2025-10-22 14:18 | 71478.875 | 80919.484 | -39111.086 | 0.87 | 0.88333 | 25624.504 | 21578.529 | 22927.188 | 29670.479 | 26973.162 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 225.36 | 226.59 | 227.734 | 49.99
2025-10-22 14:19 | 70130.219 | 82268.141 | -43157.059 | 0.85 | 0.85246 | 25624.504 | 21578.529 | 22927.188 | 29670.479 | 26973.162 | 25624.504 | -14835.239 | -16183.896 | -12137.923 | 226.073 | 227.216 | 228.317 | 49.972
2025-10-22 14:20 | 70130.219 | 80919.484 | -40459.742 | 0.86 | 0.86667 | 25624.504 | 21578.529 | 22927.188 | 29670.479 | 25624.504 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 226.634 | 227.928 | 228.835 | 49.973
2025-10-22 14:21 | 62038.273 | 71478.875 | -35065.109 | 0.86 | 0.86792 | 21578.529 | 18881.213 | 20229.871 | 25624.504 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 226.353 | 227.54 | 228.468 | 49.972
2025-10-22 14:22 | 63386.93 | 72827.539 | -35065.109 | 0.87 | 0.87037 | 21578.529 | 20229.871 | 20229.871 | 25624.504 | 24275.846 | 22927.188 | -12137.923 | -12137.923 | -10789.265 | 225.749 | 227.41 | 227.928 | 49.973
2025-10-22 14:23 | 59340.957 | 66084.242 | -29670.479 | 0.89 | 0.89796 | 20229.871 | 20229.871 | 18881.213 | 22927.188 | 21578.529 | 21578.529 | -10789.265 | -10789.265 | -9440.606 | 225.274 | 227.022 | 227.13 | 49.98
2025-10-22 14:24 | 60689.613 | 67432.906 | -29670.479 | 0.9 | 0.9 | 20229.871 | 20229.871 | 20229.871 | 22927.188 | 21578.529 | 22927.188 | -10789.265 | -9440.606 | -9440.606 | 224.994 | 226.051 | 226.677 | 49.983
2025-10-22 14:25 | 62038.273 | 70130.219 | -31019.137 | 0.89 | 0.88462 | 20229.871 | 20229.871 | 21578.529 | 22927.188 | 22927.188 | 22927.188 | -10789.265 | -10789.265 | -10789.265 | 225.037 | 226.159 | 227.173 | 49.982
2025-10-22 14:26 | 60689.613 | 68781.563 | -31019.137 | 0.89 | 0.88235 | 20229.871 | 20229.871 | 20229.871 | 22927.188 | 22927.188 | 22927.188 | -10789.265 | -9440.606 | -10789.265 | 224.584 | 226.31 | 227.216 | 49.991
2025-10-22 14:27 | 59340.957 | 66084.242 | -29670.479 | 0.9 | 0.89796 | 18881.213 | 20229.871 | 20229.871 | 21578.529 | 21578.529 | 21578.529 | -9440.606 | -9440.606 | -9440.606 | 224.713 | 226.224 | 227.087 | 49.977
2025-10-22 14:28 | 60689.613 | 68781.563 | -31019.137 | 0.89 | 0.88235 | 20229.871 | 20229.871 | 20229.871 | 22927.188 | 22927.188 | 22927.188 | -10789.265 | -10789.265 | -10789.265 | 225.77 | 227.108 | 228.166 | 49.988
2025-10-22 14:29 | 64735.586 | 71478.875 | -32367.793 | 0.89 | 0.90566 | 20229.871 | 22927.188 | 21578.529 | 22927.188 | 25624.504 | 22927.188 | -10789.265 | -10789.265 | -10789.265 | 225.253 | 226.029 | 227.626 | 49.999
2025-10-22 14:30 | 63386.93 | 70130.219 | -31019.137 | 0.9 | 0.90385 | 20229.871 | 21578.529 | 20229.871 | 22927.188 | 24275.846 | 22927.188 | -10789.265 | -10789.265 | -9440.606 | 224.886 | 225.296 | 226.979 | 50.001
2025-10-22 14:31 | 72827.539 | 82268.141 | -36413.77 | 0.89 | 0.88525 | 24275.846 | 25624.504 | 24275.846 | 26973.162 | 28321.82 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 224.994 | 225.231 | 227.389 | 50.005
2025-10-22 14:32 | 80919.484 | 91708.75 | -41808.402 | 0.88 | 0.88235 | 26973.162 | 28321.82 | 25624.504 | 31019.137 | 32367.793 | 28321.82 | -14835.239 | -16183.896 | -10789.265 | 224.562 | 225.253 | 227.605 | 49.985
2025-10-22 14:33 | 87662.773 | 99800.695 | -47203.031 | 0.88 | 0.87838 | 29670.479 | 29670.479 | 28321.82 | 33716.453 | 35065.109 | 31019.137 | -16183.896 | -17532.555 | -12137.923 | 224.648 | 225.49 | 227.842 | 49.994
2025-10-22 14:34 | 84965.461 | 97103.383 | -45854.375 | 0.88 | 0.875 | 28321.82 | 29670.479 | 26973.162 | 33716.453 | 33716.453 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 223.85 | 224.648 | 226.849 | 49.989
2025-10-22 14:35 | 87662.773 | 99800.695 | -45854.375 | 0.88 | 0.87838 | 29670.479 | 29670.479 | 28321.82 | 33716.453 | 35065.109 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 224.843 | 225.253 | 227.432 | 49.987
2025-10-22 14:36 | 79570.828 | 90360.094 | -41808.402 | 0.88 | 0.8806 | 26973.162 | 26973.162 | 25624.504 | 31019.137 | 31019.137 | 28321.82 | -14835.239 | -16183.896 | -10789.265 | 224.735 | 225.36 | 227.367 | 49.99
2025-10-22 14:37 | 76873.508 | 87662.773 | -43157.059 | 0.87 | 0.87692 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -14835.239 | -16183.896 | -12137.923 | 224.325 | 225.058 | 226.785 | 49.988
2025-10-22 14:38 | 75524.852 | 86314.117 | -41808.402 | 0.87 | 0.875 | 26973.162 | 22927.188 | 25624.504 | 31019.137 | 26973.162 | 26973.162 | -16183.896 | -14835.239 | -12137.923 | 225.015 | 225.835 | 227.281 | 49.987
2025-10-22 14:39 | 72827.539 | 82268.141 | -39111.086 | 0.87 | 0.88525 | 25624.504 | 21578.529 | 24275.846 | 29670.479 | 25624.504 | 26973.162 | -14835.239 | -13486.581 | -10789.265 | 224.023 | 224.411 | 226.116 | 49.982
2025-10-22 14:40 | 70130.219 | 79570.828 | -37762.426 | 0.88 | 0.88136 | 24275.846 | 21578.529 | 22927.188 | 28321.82 | 25624.504 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 224.217 | 224.087 | 226.029 | 49.988
2025-10-22 14:41 | 71478.875 | 82268.141 | -39111.086 | 0.88 | 0.86885 | 24275.846 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 224.303 | 225.684 | 227.281 | 49.975
2025-10-22 14:42 | 70130.219 | 80919.484 | -37762.426 | 0.88 | 0.86667 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 26973.162 | 25624.504 | -13486.581 | -13486.581 | -12137.923 | 224.627 | 225.943 | 227.518 | 49.982
2025-10-22 14:43 | 70130.219 | 78222.172 | -35065.109 | 0.89 | 0.89655 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 224.67 | 225.576 | 227.216 | 49.983
2025-10-22 14:44 | 70130.219 | 79570.828 | -37762.426 | 0.88 | 0.88136 | 24275.846 | 21578.529 | 22927.188 | 28321.82 | 25624.504 | 25624.504 | -13486.581 | -13486.581 | -10789.265 | 223.979 | 224.476 | 226.224 | 49.997
2025-10-22 14:45 | 70130.219 | 78222.172 | -36413.77 | 0.89 | 0.89655 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 223.267 | 223.807 | 225.598 | 49.998
2025-10-22 14:46 | 67432.906 | 76873.508 | -36413.77 | 0.88 | 0.87719 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 24275.846 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 224.26 | 224.972 | 226.461 | 50.013
2025-10-22 14:47 | 68781.563 | 78222.172 | -36413.77 | 0.88 | 0.87931 | 24275.846 | 21578.529 | 22927.188 | 28321.82 | 25624.504 | 25624.504 | -13486.581 | -12137.923 | -10789.265 | 224.627 | 224.756 | 226.526 | 50.019
2025-10-22 14:48 | 70130.219 | 79570.828 | -36413.77 | 0.89 | 0.88136 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 223.85 | 224.605 | 225.9 | 50.023
2025-10-22 14:49 | 76873.508 | 87662.773 | -41808.402 | 0.88 | 0.87692 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 224.303 | 225.727 | 226.828 | 50.023
2025-10-22 14:50 | 76873.508 | 87662.773 | -41808.402 | 0.87 | 0.87692 | 28321.82 | 22927.188 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -12137.923 | 224.411 | 225.188 | 226.763 | 50.019
2025-10-22 14:51 | 74176.195 | 84965.461 | -40459.742 | 0.88 | 0.87302 | 26973.162 | 22927.188 | 24275.846 | 31019.137 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 223.742 | 224.346 | 225.986 | 50.026
2025-10-22 14:52 | 71478.875 | 82268.141 | -40459.742 | 0.86 | 0.86885 | 25624.504 | 21578.529 | 22927.188 | 29670.479 | 26973.162 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 223.785 | 224.994 | 226.094 | 50.013
2025-10-22 14:53 | 71478.875 | 82268.141 | -41808.402 | 0.86 | 0.86885 | 25624.504 | 21578.529 | 24275.846 | 29670.479 | 25624.504 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 223.677 | 224.648 | 226.288 | 50.008
2025-10-22 14:54 | 74176.195 | 84965.461 | -41808.402 | 0.87 | 0.87302 | 25624.504 | 22927.188 | 24275.846 | 29670.479 | 28321.82 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 223.677 | 224.433 | 226.612 | 50.011
2025-10-22 14:55 | 74176.195 | 82268.141 | -37762.426 | 0.89 | 0.90164 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 224.195 | 224.67 | 226.547 | 49.995
2025-10-22 14:56 | 76873.508 | 86314.117 | -39111.086 | 0.89 | 0.89062 | 25624.504 | 25624.504 | 24275.846 | 29670.479 | 29670.479 | 26973.162 | -13486.581 | -14835.239 | -12137.923 | 223.375 | 224.282 | 225.857 | 49.998
2025-10-22 14:57 | 75524.852 | 86314.117 | -40459.742 | 0.88 | 0.875 | 25624.504 | 25624.504 | 24275.846 | 29670.479 | 29670.479 | 26973.162 | -13486.581 | -14835.239 | -10789.265 | 223.246 | 224.627 | 225.965 | 50.006
2025-10-22 14:58 | 72827.539 | 83616.805 | -40459.742 | 0.87 | 0.87097 | 25624.504 | 24275.846 | 22927.188 | 29670.479 | 28321.82 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 224.26 | 225.533 | 227.044 | 50.023
2025-10-22 14:59 | 71478.875 | 83616.805 | -40459.742 | 0.86 | 0.85484 | 25624.504 | 22927.188 | 22927.188 | 29670.479 | 26973.162 | 25624.504 | -14835.239 | -14835.239 | -10789.265 | 224.476 | 225.641 | 227.454 | 50.036
2025-10-22 15:00 | 72827.539 | 83616.805 | -40459.742 | 0.87 | 0.87097 | 25624.504 | 22927.188 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 223.591 | 224.67 | 226.094 | 50.027
2025-10-22 15:01 | 68781.563 | 78222.172 | -35065.109 | 0.89 | 0.87931 | 24275.846 | 21578.529 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 224.67 | 225.835 | 227.497 | 50.036
2025-10-22 15:02 | 79570.828 | 89011.43 | -40459.742 | 0.89 | 0.89394 | 26973.162 | 26973.162 | 25624.504 | 29670.479 | 31019.137 | 28321.82 | -14835.239 | -14835.239 | -10789.265 | 224.605 | 225.209 | 227.54 | 50.026
2025-10-22 15:03 | 75524.852 | 84965.461 | -37762.426 | 0.89 | 0.88889 | 25624.504 | 25624.504 | 24275.846 | 28321.82 | 29670.479 | 26973.162 | -13486.581 | -14835.239 | -10789.265 | 223.807 | 224.929 | 226.526 | 50.025
2025-10-22 15:04 | 82268.141 | 91708.75 | -41808.402 | 0.89 | 0.89706 | 26973.162 | 26973.162 | 26973.162 | 31019.137 | 31019.137 | 29670.479 | -14835.239 | -14835.239 | -12137.923 | 222.9 | 223.634 | 225.857 | 50.037
2025-10-22 15:05 | 79570.828 | 89011.43 | -40459.742 | 0.89 | 0.89394 | 25624.504 | 26973.162 | 25624.504 | 29670.479 | 31019.137 | 28321.82 | -14835.239 | -14835.239 | -12137.923 | 224.454 | 225.706 | 227.907 | 50.031
2025-10-22 15:06 | 78222.172 | 87662.773 | -39111.086 | 0.89 | 0.89231 | 25624.504 | 26973.162 | 25624.504 | 29670.479 | 29670.479 | 28321.82 | -13486.581 | -14835.239 | -10789.265 | 223.483 | 224.303 | 226.116 | 50.023
2025-10-22 15:07 | 78222.172 | 87662.773 | -40459.742 | 0.89 | 0.89231 | 26973.162 | 26973.162 | 25624.504 | 29670.479 | 31019.137 | 28321.82 | -13486.581 | -14835.239 | -10789.265 | 223.224 | 224.325 | 225.986 | 50.008
2025-10-22 15:08 | 86314.117 | 97103.383 | -45854.375 | 0.88 | 0.88889 | 29670.479 | 26973.162 | 28321.82 | 35065.109 | 32367.793 | 31019.137 | -16183.896 | -16183.896 | -12137.923 | 224.26 | 225.36 | 226.871 | 49.99
2025-10-22 15:09 | 80919.484 | 93057.406 | -43157.059 | 0.88 | 0.86957 | 29670.479 | 24275.846 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 225.447 | 226.483 | 227.972 | 49.996
2025-10-22 15:10 | 78222.172 | 90360.094 | -43157.059 | 0.87 | 0.86567 | 28321.82 | 24275.846 | 26973.162 | 32367.793 | 28321.82 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 224.907 | 226.008 | 227.497 | 50.002
2025-10-22 15:11 | 82268.141 | 94406.063 | -44505.715 | 0.88 | 0.87143 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.605 | 225.598 | 227.432 | 50.005
2025-10-22 15:12 | 84965.461 | 97103.383 | -45854.375 | 0.88 | 0.875 | 29670.479 | 26973.162 | 28321.82 | 35065.109 | 31019.137 | 31019.137 | -16183.896 | -16183.896 | -13486.581 | 224.799 | 226.073 | 227.713 | 50.009
2025-10-22 15:13 | 80919.484 | 91708.75 | -43157.059 | 0.88 | 0.88235 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 224.195 | 225.598 | 227.195 | 50.002
2025-10-22 15:14 | 83616.805 | 95754.727 | -44505.715 | 0.88 | 0.87324 | 29670.479 | 25624.504 | 28321.82 | 33716.453 | 29670.479 | 31019.137 | -16183.896 | -16183.896 | -12137.923 | 224.109 | 225.166 | 227 | 49.999
2025-10-22 15:15 | 82268.141 | 94406.063 | -45854.375 | 0.87 | 0.87143 | 29670.479 | 25624.504 | 26973.162 | 33716.453 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.303 | 225.188 | 227.13 | 50.006
2025-10-22 15:16 | 79570.828 | 91708.75 | -44505.715 | 0.86 | 0.86765 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 223.979 | 224.972 | 226.418 | 49.996
2025-10-22 15:17 | 80919.484 | 93057.406 | -45854.375 | 0.87 | 0.86957 | 28321.82 | 26973.162 | 25624.504 | 32367.793 | 31019.137 | 28321.82 | -16183.896 | -16183.896 | -12137.923 | 223.203 | 224.325 | 225.835 | 49.983
2025-10-22 15:18 | 82268.141 | 94406.063 | -44505.715 | 0.87 | 0.87143 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 223.699 | 224.886 | 226.634 | 49.997
2025-10-22 15:19 | 80919.484 | 94406.063 | -47203.031 | 0.86 | 0.85714 | 28321.82 | 25624.504 | 26973.162 | 33716.453 | 31019.137 | 29670.479 | -17532.555 | -17532.555 | -13486.581 | 224.843 | 225.555 | 227.626 | 50
2025-10-22 15:20 | 75524.852 | 87662.773 | -43157.059 | 0.87 | 0.86154 | 26973.162 | 24275.846 | 24275.846 | 31019.137 | 29670.479 | 26973.162 | -14835.239 | -16183.896 | -12137.923 | 224.217 | 225.404 | 227.432 | 49.987
2025-10-22 15:21 | 75524.852 | 86314.117 | -41808.402 | 0.87 | 0.875 | 26973.162 | 24275.846 | 24275.846 | 31019.137 | 28321.82 | 26973.162 | -14835.239 | -16183.896 | -10789.265 | 224.584 | 225.598 | 227.648 | 49.988
2025-10-22 15:22 | 72827.539 | 83616.805 | -40459.742 | 0.87 | 0.87097 | 24275.846 | 24275.846 | 24275.846 | 28321.82 | 28321.82 | 26973.162 | -14835.239 | -14835.239 | -12137.923 | 224.864 | 225.878 | 227.928 | 49.985
2025-10-22 15:23 | 67432.906 | 76873.508 | -35065.109 | 0.89 | 0.87719 | 22927.188 | 22927.188 | 21578.529 | 25624.504 | 26973.162 | 24275.846 | -12137.923 | -12137.923 | -10789.265 | 223.785 | 225.145 | 226.914 | 49.992
2025-10-22 15:24 | 70130.219 | 78222.172 | -36413.77 | 0.89 | 0.89655 | 24275.846 | 22927.188 | 22927.188 | 26973.162 | 25624.504 | 25624.504 | -12137.923 | -12137.923 | -10789.265 | 224.195 | 225.555 | 226.763 | 49.985
2025-10-22 15:25 | 74176.195 | 83616.805 | -37762.426 | 0.89 | 0.8871 | 25624.504 | 24275.846 | 24275.846 | 29670.479 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 224.001 | 224.843 | 226.094 | 49.987
2025-10-22 15:26 | 75524.852 | 84965.461 | -39111.086 | 0.89 | 0.88889 | 25624.504 | 24275.846 | 25624.504 | 29670.479 | 28321.82 | 28321.82 | -13486.581 | -13486.581 | -12137.923 | 223.893 | 225.598 | 226.569 | 49.984
2025-10-22 15:27 | 76873.508 | 86314.117 | -39111.086 | 0.89 | 0.89062 | 26973.162 | 24275.846 | 25624.504 | 29670.479 | 28321.82 | 28321.82 | -13486.581 | -13486.581 | -12137.923 | 224.735 | 226.051 | 227.195 | 49.975
2025-10-22 15:28 | 72827.539 | 82268.141 | -37762.426 | 0.89 | 0.88525 | 25624.504 | 24275.846 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -12137.923 | 224.907 | 226.504 | 227.648 | 49.992
2025-10-22 15:29 | 72827.539 | 82268.141 | -37762.426 | 0.89 | 0.88525 | 25624.504 | 22927.188 | 24275.846 | 28321.82 | 26973.162 | 26973.162 | -13486.581 | -13486.581 | -10789.265 | 224.864 | 226.116 | 227.432 | 49.995
2025-10-22 15:30 | 76873.508 | 86314.117 | -40459.742 | 0.88 | 0.89062 | 26973.162 | 24275.846 | 25624.504 | 29670.479 | 28321.82 | 28321.82 | -14835.239 | -13486.581 | -12137.923 | 224.713 | 225.922 | 227.626 | 50.006
2025-10-22 15:31 | 79570.828 | 90360.094 | -44505.715 | 0.87 | 0.8806 | 28321.82 | 24275.846 | 25624.504 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.015 | 226.051 | 228.079 | 49.998
2025-10-22 15:32 | 79570.828 | 90360.094 | -43157.059 | 0.88 | 0.8806 | 28321.82 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 28321.82 | -14835.239 | -16183.896 | -12137.923 | 224.756 | 226.159 | 228.187 | 50.011
2025-10-22 15:33 | 84965.461 | 97103.383 | -45854.375 | 0.88 | 0.875 | 29670.479 | 28321.82 | 26973.162 | 33716.453 | 32367.793 | 29670.479 | -16183.896 | -17532.555 | -12137.923 | 224.648 | 225.447 | 227.864 | 50.022
2025-10-22 15:34 | 84965.461 | 95754.727 | -44505.715 | 0.88 | 0.88732 | 29670.479 | 26973.162 | 26973.162 | 33716.453 | 32367.793 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 224.13 | 224.346 | 227.065 | 50.027
2025-10-22 15:35 | 84965.461 | 97103.383 | -45854.375 | 0.88 | 0.875 | 29670.479 | 28321.82 | 28321.82 | 33716.453 | 33716.453 | 31019.137 | -16183.896 | -17532.555 | -12137.923 | 224.95 | 225.857 | 227.972 | 50.028
2025-10-22 15:36 | 83616.805 | 94406.063 | -44505.715 | 0.88 | 0.88571 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 32367.793 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 225.274 | 226.159 | 228.209 | 50.016
2025-10-22 15:37 | 82268.141 | 93057.406 | -44505.715 | 0.88 | 0.88406 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 223.936 | 224.778 | 226.763 | 49.994
2025-10-22 15:38 | 76873.508 | 87662.773 | -41808.402 | 0.88 | 0.87692 | 26973.162 | 24275.846 | 25624.504 | 31019.137 | 28321.82 | 28321.82 | -14835.239 | -14835.239 | -10789.265 | 224.821 | 225.9 | 227.626 | 50.002
2025-10-22 15:39 | 76873.508 | 89011.43 | -41808.402 | 0.87 | 0.86364 | 28321.82 | 22927.188 | 25624.504 | 32367.793 | 28321.82 | 28321.82 | -16183.896 | -14835.239 | -10789.265 | 224.54 | 225.706 | 227.367 | 49.979
2025-10-22 15:40 | 80919.484 | 91708.75 | -41808.402 | 0.88 | 0.88235 | 29670.479 | 24275.846 | 26973.162 | 32367.793 | 28321.82 | 29670.479 | -16183.896 | -14835.239 | -10789.265 | 224.54 | 225.727 | 227.216 | 49.979
2025-10-22 15:41 | 82268.141 | 93057.406 | -43157.059 | 0.88 | 0.88406 | 29670.479 | 25624.504 | 26973.162 | 32367.793 | 29670.479 | 29670.479 | -16183.896 | -14835.239 | -12137.923 | 224.778 | 226.439 | 227.734 | 49.981
2025-10-22 15:42 | 82268.141 | 94406.063 | -44505.715 | 0.88 | 0.87143 | 28321.82 | 26973.162 | 26973.162 | 32367.793 | 31019.137 | 29670.479 | -16183.896 | -16183.896 | -12137.923 | 223.85 | 225.253 | 226.763 | 49.986
2025-10-22 15:43 | 75524.852 | 84965.461 | -39111.086 | 0.88 | 0.88889 | 26973.162 | 24275.846 | 24275.846 | 29670.479 | 28321.82 | 26973.162 | -14835.239 | -14835.239 | -10789.265 | 223.936 | 225.015 | 226.396 | 49.977
2025-10-22 15:44 | 79570.828 | 90360.094 | -41808.402 | 0.88 | 0.8806 | 28321.82 | 25624.504 | 25624.504 | 32367.793 | 29670.479 | 28321.82 | -16183.896 | -14835.239 | -10789.265 | 224.519 | 224.886 | 226.914 | 49.99
2025-10-22 15:45 | 72827.539 | 82268.141 | -39111.086 | 0.88 | 0.88525 | 25624.504 | 22927.188 | 24275.846 | 29670.479 | 26973.162 | 25624.504 | -14835.239 | -14835.239 | -9440.606 | 223.828 | 224.519 | 226.849 | 50.009
2025-10-22 15:46 | 72827.539 | 82268.141 | -37762.426 | 0.88 | 0.88525 | 25624.504 | 22927.188 | 24275.846 | 29670.479 | 26973.162 | 25624.504 | -14835.239 | -13486.581 | -9440.606 | 224.476 | 225.08 | 227.562 | 50.017
2025-10-22 15:47 | 72827.539 | 82268.141 | -37762.426 | 0.88 | 0.88525 | 25624.504 | 22927.188 | 24275.846 | 29670.479 | 26973.162 | 25624.504 | -14835.239 | -13486.581 | -9440.606 | 223.893 | 223.979 | 226.547 | 50.023
2025-10-22 15:48 | 71478.875 | 82268.141 | -39111.086 | 0.87 | 0.86885 | 25624.504 | 22927.188 | 22927.188 | 29670.479 | 26973.162 | 25624.504 | -14835.239 | -14835.239 | -9440.606 | 224.886 | 225.663 | 227.842 | 50.024
2025-10-22 15:49 | 66084.242 | 76873.508 | -39111.086 | 0.86 | 0.85965 | 24275.846 | 20229.871 | 21578.529 | 28321.82 | 24275.846 | 24275.846 | -14835.239 | -13486.581 | -10789.265 | 227.669 | 228.338 | 230.194 | 50.01
2025-10-22 15:50 | 59340.957 | 67432.906 | -33716.453 | 0.87 | 0.88 | 21578.529 | 17532.555 | 18881.213 | 24275.846 | 21578.529 | 21578.529 | -12137.923 | -12137.923 | -9440.606 | 227.432 | 227.928 | 229.396 | 50.013
2025-10-22 15:51 | 55294.98 | 63386.93 | -29670.479 | 0.88 | 0.87234 | 20229.871 | 17532.555 | 18881.213 | 22927.188 | 20229.871 | 20229.871 | -10789.265 | -10789.265 | -8091.948 | 227.087 | 228.209 | 229.051 | 50.007
2025-10-22 15:52 | 56643.641 | 63386.93 | -28321.82 | 0.9 | 0.89362 | 18881.213 | 18881.213 | 18881.213 | 21578.529 | 21578.529 | 21578.529 | -9440.606 | -9440.606 | -9440.606 | 226.936 | 228.274 | 229.202 | 49.994
2025-10-22 15:53 | 57992.297 | 63386.93 | -26973.162 | 0.9 | 0.91489 | 18881.213 | 18881.213 | 18881.213 | 21578.529 | 21578.529 | 21578.529 | -9440.606 | -9440.606 | -9440.606 | 227.13 | 228.166 | 229.245 | 49.996
2025-10-22 15:54 | 59340.957 | 66084.242 | -28321.82 | 0.9 | 0.89796 | 20229.871 | 18881.213 | 20229.871 | 22927.188 | 21578.529 | 21578.529 | -10789.265 | -9440.606 | -8091.948 | 225.706 | 226.547 | 228.187 | 49.979
2025-10-22 15:55 | 62038.273 | 70130.219 | -32367.793 | 0.89 | 0.88462 | 21578.529 | 20229.871 | 20229.871 | 24275.846 | 22927.188 | 22927.188 | -12137.923 | -12137.923 | -9440.606 | 226.332 | 227.41 | 228.748 | 49.984
2025-10-22 15:56 | 57992.297 | 66084.242 | -32367.793 | 0.87 | 0.87755 | 20229.871 | 17532.555 | 18881.213 | 22927.188 | 21578.529 | 21578.529 | -12137.923 | -10789.265 | -9440.606 | 226.828 | 227.669 | 229.158 | 49.983
2025-10-22 15:57 | 64735.586 | 74176.195 | -33716.453 | 0.89 | 0.87273 | 22927.188 | 21578.529 | 21578.529 | 25624.504 | 24275.846 | 24275.846 | -12137.923 | -12137.923 | -9440.606 | 226.18 | 227.626 | 228.727 | 49.992
2025-10-22 15:58 | 62038.273 | 70130.219 | -32367.793 | 0.89 | 0.88462 | 21578.529 | 20229.871 | 20229.871 | 24275.846 | 22927.188 | 21578.529 | -10789.265 | -12137.923 | -9440.606 | 225.619 | 227.648 | 227.756 | 50.013
2025-10-22 15:59 | 55294.98 | 62038.273 | -29670.479 | 0.87 | 0.8913 | 18881.213 | 17532.555 | 17532.555 | 21578.529 | 21578.529 | 18881.213 | -10789.265 | -10789.265 | -8091.948 | 225.706 | 226.806 | 228.166 | 50.027
2025-10-22 16:00 | 55294.98 | 63386.93 | -31019.137 | 0.87 | 0.87234 | 18881.213 | 18881.213 | 17532.555 | 21578.529 | 22927.188 | 20229.871 | -10789.265 | -12137.923 | -8091.948 | 226.698 | 227.13 | 229.482 | 50.033

## data_quality
Rank | Interval (s) | Count | Percent
Interval 1 | 60.0 | 1,439 | 99.93

## mapping_log
target | source | index
DPF_total | Klasický DPF Celkom Priem | 171
F | Frekvencia Priem | 99
PF_total | Klasický PF Celkom Priem | 159
P_L1N | Činný výkon L1N Priem | 114
P_L2N | Činný výkon L2N Priem | 117
P_L3N | Činný výkon L3N Priem | 120
P_total | Činný výkon Celkom Priem | 123
Q_L1N | Klasické VAR L1N Priem | 138
Q_L2N | Klasické VAR L2N Priem | 141
Q_L3N | Klasické VAR L3N Priem | 144
Q_total | Klasické VAR Celkom Priem | 147
S_L1N | Klasický VA full L1N Priem | 126
S_L2N | Klasický VA full L2N Priem | 129
S_L3N | Klasický VA full L3N Priem | 132
S_total | Klasický VA full Celkom Priem | 135
THD_A_L1 | THD A L1 Priem | 974
THD_A_L2 | THD A L2 Priem | 977
THD_A_L3 | THD A L3 Priem | 980
THD_V_L1N | THD V L1N Priem | 174
THD_V_L2N | THD V L2N Priem | 177
THD_V_L3N | THD V L3N Priem | 180
U_L1N | Napätie L1N Priem | 3
U_L2N | Napätie L2N Priem | 6
U_L3N | Napätie L3N Priem | 9
cas | Čas | 1
datum | Dátum | 0